## Sheet1
Last_Letter | Last_Letter Description (NL) | Last_Letter Description (EN) | Last_Letter Brick Class
A-- | Alarm | Alarm | Alarm
AB- | brandmelding RK-01 BMC | Fire alarm RK-01 BMC | Fire_Sensor
AI- | installatie automaten | Fuse | Switchgear
AN- | netwachter | Power phase monitor (alarm) | Power_Loss_Alarm
AS- | sabotage | sabotage
B-- | Bedrijfsmelding | Operation status | Status
BI- | herinschakelen ventilatie na brand | restart ventilation after fire | Reset_Command
BR- | reset storing | reset failure | Reset_Command
BS- | spanningsbewaking stuurstroom (NC) | voltage monitoring of control current (NC) | Voltage
BU- | heruitschakelen ventilatie na brand | turn off ventilation after fire | Off_Command
BV- | voeding aanwezig | power supply present | Power_Sensor
D-- | Dicht | Closed | Open_Close_Status
HS-- | Hoofdschakelaar | Main switch | Switchgear
L-- | Lokaal bediend | Locally operated | Status
L-- | regelkast lokaal bediend | switch box locally controlled | Switchgear
LG-- | Lichtgroep | Light Group | Lighting
M-- | Meting | Measurement | Sensor
O-- | Open | Open | Open_Close_Status
S-- | Schakelen | Switch | Status
SB- | brandsturing | Fire control | Fire_Control_Panel
SI- | brandschakelaar ventilatie in | fire switch ventilation on command | Fire_Control_Panel
SN- | niet urgente storingsmelding | non-urgent failure status | Failure_Alarm
SR- | reset op afstand (GBS) | Remote reset (BMS) | Reset_Command
SRP | resetplus | resetplus | Reset_Command
SS- | staffel relais | Switching on in a cascading manner
SU- | urgente storing | Urgent failure | Failure_Alarm
SU- | brandschakelaar ventilatie uit | fire switch ventilation off command | Fire_Control_Panel
T-- | Telling(er) | Count | Meter
V-- | Sturing | Control (analog signal) | Command
W-- | Werksetpunt | Operation set point | Setpoint
WS- | Werkschakelaar | Operation switch (small switchgear) | Switchgear
X-- | Instelling (X-as) | Configuration (X-axis) | Setpoint
XS- | Setpunt verstelling | Adjustment set point | Setpoint
Y-- | Instelling (Y-as) | Configuration (Y-axis) | Setpoint

## Sheet1 (2)
NL | EN
A-- |  | Alarm
Alarm | Alarm
B-- |  | Alarm
Bedrijfsmelding | Operation alarm
D-- |  | Status
Dicht | Closed
HS--
Hoofdschakelaar | Main switch
L--
Lokaal bediend | Locally operated
LG--
Lichtgroep | Light Group | Lighting_System
M--
Meting | Measurement | Point
O-- |  | Status
Open | Open
S--
Schakelen | Switch
T--
Telling(er) | Count | Status
V--
Sturing | Control
WS-
Werkschakelaar | Operation switch
W-- |  | Setpoint
Werksetpunt | Operation set point
X--
Instelling (X-as) | Configuration (X-axis)
XS- |  | Setpoint
Setpunt verstelling | Adjustment set point
Y--
Instelling (Y-as) | Configuration (Y-axis)
SU-
urgente storing | Urgent failure
SN-
niet urgente storingsmelding | non-urgent failure alarm
SR-
reset op afstand (GBS) | Remote reset (BMS)
SB-
brandsturing | Fire control
SI-
brandschakelaar ventilatie in | fire switch ventilation on
SU-
brandschakelaar ventilatie uit | fire switch ventilation off
SS-
staffel relais | scaled relay
SRP
resetplus | resetplus
BR-
reset storing | reset failure
BI-
herinschakelen ventilatie na brand | restart ventilation after fire
BU-
heruitschakelen ventilatie na brand | turn off ventilation after fire
BV-
voeding aanwezig | supply present
L--
regelkast lokaal bediend | switch box locally controlled
BS-
spanningsbewaking stuurstroom (NC) | voltage monitoring of control current (NC) | NC = normally closed
AB-
brandmelding RK-01 BMC | Fire alarm RK-01 BMC | RK = switch box; BMC = brandmeldcentrale (Fire alarm central)
AN-
netwachter | phase monitor
AS-
sabotage | sabotage
AI-
installatie automaten | installation machines