## Sheet1
| Item Reference | Object ID | Object Type | Name | Num | Code | Last_Letter | Description (NL) | Description (EN) | Num Class Brick | Num Description (NL) | Num Description (EN) | Num Brick | Code Description (NL) | Code Description (EN) | Code Brick Class | Last_Letter Description (NL) | Last_Letter Description (EN) | Last_Letter Brick Class
0 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SM1-CL | SM1-CL | BI Mapper | (33) 402.CV-01D-- | 402 | cv | d | Wisselklep bronnen dicht | Diverter valve sources closed | Energy_Storage | Koudebron | Cold source | Energy_Storage | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
1 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM1-CL | SM1-CL | BI Mapper | (33) 404.CV-01D-- | 404 | cv | d | Wisselklep drogekoeler dicht | Drycooler reversing valve closed | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
2 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.BK-01-D | BK-01-D | BI Mapper | (33) 203.BK-01D--(reserve) | 203 | bk | d | Brandkleppen dicht bgg | Fire dampers closed bgg | AHU |  |  |  |  | Firedamper | Damper | Dicht | Closed | Open_Close_Status
3 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Spuiklep riool status dicht | Spuiklep riool status dicht | BI Mapper | (33) 413.CV-01D-- | 413 | cv | d | Spuiklep riool status dicht | Drain valve sewer status closed | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
4 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SM2-CL | SM2-CL | BI Mapper | (33) 402.CV-02D-- | 402 | cv | d | Wisselklep bronnen dicht | Diverter valve sources closed | Energy_Storage | Koudebron | Cold source | Energy_Storage | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
5 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM2-CL | SM2-CL | BI Mapper | (33) 404.CV-02D-- | 404 | cv | d | Wisselklep drogekoeler dicht | Drycooler reversing valve closed | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
6 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.BK-02-D | BK-02-D | BI Mapper | (33) 203.BK-02D-- | 203 | bk | d | Brandkleppen dicht cluster 1-1 | Fire dampers closed cluster 1-1 | AHU |  |  |  |  | Firedamper | Damper | Dicht | Closed | Open_Close_Status
7 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.HTGVALVE-CL | HTGVALVE-CL | BI Mapper | (33) 021.CV-03D-- | 021 | cv | d | Vlinderklep CV dicht | Butterfly valve CV closed | Hot_Water_System | Warm water groep 1 | Hot water group 1 | Hot_Water_System | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
8 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.HTGVALVE-CL | HTGVALVE-CL | BI Mapper | (33) 022.CV-03D-- | 022 | cv | d | Vlinderklep CV dicht | Butterfly valve CV closed | Hot_Water_System | Warm water groep 2 | Hot water group 2 | Hot_Water_System | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
9 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SM3-CL | SM3-CL | BI Mapper | (33) 402.CV-03D-- | 402 | cv | d | Wisselklep bronnen dicht | Diverter valve sources closed | Energy_Storage | Koudebron | Cold source | Energy_Storage | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
10 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM3-CL | SM3-CL | BI Mapper | (33) 404.CV-03D-- | 404 | cv | d | Wisselklep drogekoeler dicht | Drycooler reversing valve closed | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
11 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.BK-03-D | BK-03-D | BI Mapper | (33) 203.BK-03D-- | 203 | bk | d | Brandkleppen dicht cluster 1-2 | Fire dampers closed cluster 1-2 | AHU |  |  |  |  | Firedamper | Damper | Dicht | Closed | Open_Close_Status
12 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.HTGV-CL | HTGV-CL | BI Mapper | (33) 201.CV-03D-- | 201 | cv | d | Vlinderklep CV dicht | Butterfly valve CV closed | AHU | LBK 1 | AHU 1 | AHU | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
13 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.HTGV-CL | HTGV-CL | BI Mapper | (33) 202.CV-03D-- | 202 | cv | d | Vlinderklep CV dicht | Butterfly valve CV closed | AHU | LBK 2 | AHU 2 | AHU | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
14 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CLGVALVE-CL | CLGVALVE-CL | BI Mapper | (33) 021.CV-04D-- | 021 | cv | d | Vlinderklep GKW dicht | Butterfly valve GKW closed | Hot_Water_System | Warm water groep 1 | Hot water group 1 | Hot_Water_System | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
15 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.CLGVALVE-CL | CLGVALVE-CL | BI Mapper | (33) 022.CV-04D-- | 022 | cv | d | Vlinderklep GKW dicht | Butterfly valve GKW closed | Hot_Water_System | Warm water groep 2 | Hot water group 2 | Hot_Water_System | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
16 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SM4-CL | SM4-CL | BI Mapper | (33) 402.CV-04D-- | 402 | cv | d | Wisselklep bronnen dicht | Diverter valve sources closed | Energy_Storage | Koudebron | Cold source | Energy_Storage | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
17 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM4-CL | SM4-CL | BI Mapper | (33) 404.CV-04D-- | 404 | cv | d | Wisselklep drogekoeler dicht | Drycooler reversing valve closed | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
18 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.BK-04-D | BK-04-D | BI Mapper | (33) 203.BK-04D-- | 203 | bk | d | Brandkleppen dicht cluster 2-1 | Fire dampers closed cluster 2-1 | AHU |  |  |  |  | Firedamper | Damper | Dicht | Closed | Open_Close_Status
19 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CLGV-CL | CLGV-CL | BI Mapper | (33) 201.CV-04D-- | 201 | cv | d | Vlinderklep GKW dicht | Butterfly valve GKW closed | AHU | LBK 1 | AHU 1 | AHU | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
20 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.CLGV-CL | CLGV-CL | BI Mapper | (33) 202.CV-04D-- | 202 | cv | d | Vlinderklep GKW dicht | Butterfly valve GKW closed | AHU | LBK 2 | AHU 2 | AHU | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
21 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM5-CL | SM5-CL | BI Mapper | (33) 404.CV-05D-- | 404 | cv | d | Wisselklep drogekoeler dicht | Drycooler reversing valve closed | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
22 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.BK-05-D | BK-05-D | BI Mapper | (33) 203.BK-05D-- | 203 | bk | d | Brandkleppen dicht cluster 2-2 | Fire dampers closed cluster 2-2 | AHU |  |  |  |  | Firedamper | Damper | Dicht | Closed | Open_Close_Status
23 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM6-CL | SM6-CL | BI Mapper | (33) 404.CV-06D-- | 404 | cv | d | Wisselklep drogekoeler dicht | Drycooler reversing valve closed | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
24 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.BK-06-D | BK-06-D | BI Mapper | (33) 203.BK-06D-- | 203 | bk | d | Brandkleppen dicht cluster 3-1 | Fire dampers closed cluster 3-1 | AHU |  |  |  |  | Firedamper | Damper | Dicht | Closed | Open_Close_Status
25 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM7-CL | SM7-CL | BI Mapper | (33) 404.CV-07D-- | 404 | cv | d | Wisselklep drogekoeler dicht | Drycooler reversing valve closed | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Dicht | Closed | Open_Close_Status
26 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.BK-07-D | BK-07-D | BI Mapper | (33) 203.BK-07D-- | 203 | bk | d | Brandkleppen dicht cluster 3-2 | Fire dampers closed cluster 3-2 | AHU |  |  |  |  | Firedamper | Damper | Dicht | Closed | Open_Close_Status
27 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SHWP1-FAULT | SHWP1-FAULT | BI Mapper | (33) 001.TP-01A-- | 001 | tp | a | Transportpomp 1 storing | Transport pump 1 malfunction | Boiler | Ketel 1 | Boiler 1 | Boiler | Transportpomp | Transport pump | Pump | Alarm | Alarm | Alarm
28 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.LA1-A | LA1-A | BI Mapper | (33) 901.LA-01A-- | 901 | la | a | Wateroverlast technische ruimte | Flooding technical room | Water_Loss_Alarm | Wateroverlast | Flooding water spill | Water_Loss_Alarm | Niveau alarm | Level alarm | Water_Level_Alarm | Alarm | Alarm | Alarm
29 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.MISC-A1 | MISC-A1 | BI Mapper | (33) 902.LV-01A-- | 902 | lv | a | Tracing vetvangleiding groep 1 storing | Tracing grease trap line group 1 malfunction | [5 empty] | Tracing grease trap line |  | Alarm | Alarm | Alarm
30 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Ontruiming-A | Ontruiming-A | BI Mapper | (33) 917.XA-01A-- | 917 | xa | a | Ontruimingsinstal. storing urgent | Evacuation system malfunction urgent |  |  |  |  | Storing algemeen | Malfunction general | Fault_Status | Alarm | Alarm | Alarm
31 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.KNXNU-A | KNXNU-A | BI Mapper | (33) 918.XA-01A-- | 918 | xa | a | KNX installatie storing niet urgent | KNX installation fault not urgent |  |  |  |  | Storing algemeen | Malfunction general | Fault_Status | Alarm | Alarm | Alarm
32 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.HCP-A | HCP-A | BI Mapper | (33) 021.CP-01A-- | 021 | cp | a | Circulatiepomp storing | Circulation pump failure | Hot_Water_System | Warm water groep 1 | Hot water group 1 | Hot_Water_System | Circulatie pomp | Circulation pump | Pump | Alarm | Alarm | Alarm
33 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.HCP-A | HCP-A | BI Mapper | (33) 022.CP-01A-- | 022 | cp | a | Circulatiepomp storing | Circulation pump failure | Hot_Water_System | Warm water groep 2 | Hot water group 2 | Hot_Water_System | Circulatie pomp | Circulation pump | Pump | Alarm | Alarm | Alarm
34 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Parameters.Vetvanger 1 tracing storing | Vetvanger 1 tracing storing | MSV Mapper | (33) 902.LV-01A-- | 902 | lv | a | Vetvanger 1 tracing storing | Grease trap 1 tracing failure | [5 empty] | Tracing grease trap line |  | Alarm | Alarm | Alarm
35 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWP-FAULT | SCHWP-FAULT | BI Mapper | (33) 121.CP-01A-- | 121 | cp | a | Circulatiepomp storing | Circulation pump failure | Chilled_Water_System | Gekoeld water groep 1 | Chilled water group 1 | Chilled_Water_System | Circulatie pomp | Circulation pump | Pump | Alarm | Alarm | Alarm
36 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWP1-FAULT | SCHWP1-FAULT | BI Mapper | (33) 122.TP-01A-- | 122 | tp | a | Transportpomp 1 storing | Transport pump 1 malfunction | Chilled_Water_System | Gekoeld water groep 2 | Chilled water group 2 | Chilled_Water_System | Transportpomp | Transport pump | Pump | Alarm | Alarm | Alarm
37 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CHWF-A | CHWF-A | BI Mapper | (33) 402.FT-01A-- | 402 | ft | a | Flowmeter laden/ontladen storing | Flowmeter charge/discharge fault | Energy_Storage | Koudebron | Cold source | Energy_Storage | Flow transmitter | flow transmitter | Water_Meter | Alarm | Alarm | Alarm
38 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.TP-FAULT | TP-FAULT | BI Mapper | (33) 402.TP-01A-- | 402 | tp | a | Transportpomp bronnen storing | Transfer pump sources failure | Energy_Storage | Koudebron | Cold source | Energy_Storage | Transportpomp | Transport pump | Pump | Alarm | Alarm | Alarm
39 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CH1-A | CH1-A | BI Mapper | (33) 403.WP-01A-- | 403 | wp | a | Warmtepomp storing | Heat pump malfunction | Energy_Storage |  |  |  | Warmtepomp | Heat pump | Equipment | Alarm | Alarm | Alarm
40 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CWP1-FAULT | CWP1-FAULT | BI Mapper | (33) 403.CP-01A-- | 403 | cp | a | Circulatiepomp WP-CV storing | Circulation pump WP-CV malfunction | Energy_Storage |  |  |  | Circulatie pomp | Circulation pump | Pump | Alarm | Alarm | Alarm
41 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CWP1-FAULT | CWP1-FAULT | BI Mapper | (33) 404.CP-01A-- | 404 | cp | a | Circulatiepomp drogekoeler prim. storing | Circulation pump dry cooler prim. malfunction | Energy_Storage |  |  |  | Circulatie pomp | Circulation pump | Pump | Alarm | Alarm | Alarm
42 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CT1-FAULT | CT1-FAULT | BI Mapper | (33) 404.DK-01A-- | 404 | dk | a | Drogekoeler storing | Drycooler malfunction | Energy_Storage |  |  |  | Doseer klep | Dosing valve | Valve | Alarm | Alarm | Alarm
43 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.302-AV1-A | 302-AV1-A | BI Mapper | (33) 302.VA-01A-- | 302 | va | a | Afzuigventilator containerruimte stor | Exhaust fan container space stor | Exhaust_Fan | Afzuig toiletten | Exhaust fan for toilets | Exhaust_Fan | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Alarm | Alarm | Alarm
44 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.301-AV1-A | 301-AV1-A | BI Mapper | (33) 301.VA-01A-- | 301 | va | a | Afzuigventilator horeca links storing | Exhaust fan catering left malfunction | Exhaust_Fan | Afzuig liftmachinekamer | Exhaust fan for machine room of elevator | Exhaust_Fan | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Alarm | Alarm | Alarm
45 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.HRW-FAULT | HRW-FAULT | BI Mapper | (33) 201.WW-01A-- | 201 | ww | a | Warmtewiel storing | Heat wheel failure | AHU | LBK 1 | AHU 1 | AHU | Warmtewiel | Rotary heat recovery | Heat_Wheel | Alarm | Alarm | Alarm
46 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.LT-A | LT-A | BI Mapper | (33) 201.TA-01A-- | 201 | ta | a | Vorstthermostaat | Frost thermostat | AHU | LBK 1 | AHU 1 | AHU | Temperatuur alarm | Temperature alarm | Temperature_Alarm | Alarm | Alarm | Alarm
47 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.PHP-OL | PHP-OL | BI Mapper | (33) 201.CP-01A-- | 201 | cp | a | Circulatiepomp storing | Circulation pump failure | AHU | LBK 1 | AHU 1 | AHU | Circulatie pomp | Circulation pump | Pump | Alarm | Alarm | Alarm
48 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.HRW-FAULT | HRW-FAULT | BI Mapper | (33) 202.WW-01A-- | 202 | ww | a | Warmtewiel storing | Heat wheel failure | AHU | LBK 2 | AHU 2 | AHU | Warmtewiel | Rotary heat recovery | Heat_Wheel | Alarm | Alarm | Alarm
49 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.LT-A | LT-A | BI Mapper | (33) 202.TA-01A-- | 202 | ta | a | Vorstthermostaat | Frost thermostat | AHU | LBK 2 | AHU 2 | AHU | Temperatuur alarm | Temperature alarm | Temperature_Alarm | Alarm | Alarm | Alarm
50 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.PHP-OL | PHP-OL | BI Mapper | (33) 202.CP-01A-- | 202 | cp | a | Circulatiepomp storing | Circulation pump failure | AHU | LBK 2 | AHU 2 | AHU | Circulatie pomp | Circulation pump | Pump | Alarm | Alarm | Alarm
51 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.SF-BA | SF-BA | MSV Mapper | (33) 201.PDA-01A-- | 201 | pda | a | Flow alarm toevoerventilator | Supply fan flow alarm | AHU | LBK 1 | AHU 1 | AHU | Drukverschil alarm | Pressure difference alarm | Pressure_Alarm | Alarm | Alarm | Alarm
52 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Parameters.SF-BA | SF-BA | MSV Mapper | (33) 202.PDA-01A-- | 202 | pda | a | Flow alarm toevoerventilator | Supply fan flow alarm | AHU | LBK 2 | AHU 2 | AHU | Drukverschil alarm | Pressure difference alarm | Pressure_Alarm | Alarm | Alarm | Alarm
53 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.HXCWP1-A | HXCWP1-A | BI Mapper | (33) 903.HYD01A-- | 903 | hyd | a | Hydrofoor stroring urgent | Pressurized water failure urgent |  |  |  |  | Hydrofoor installatie | Pressurized water installation Hydrophore installation to maintain water pressure |  | Alarm | Alarm | Alarm
54 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.OG-A | OG-A | BI Mapper | (33).041.OG-01A-- | 041 | og | a | Ontgasser storing | Degasser malfunction | Hot_Water_System |  |  |  |  | Degasser |  | Alarm | Alarm | Alarm
55 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Sprinkler-A1 | Sprinkler-A1 | BI Mapper | (33) 501.XA-01A1- | 501 | xa | a | Sprinkeler storing | Sprinkler malfunction | Sprinkler |  | Sprinker | Fire_Safety_System | Storing algemeen | Malfunction general | Fault_Status | Alarm | Alarm | Alarm
56 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Parameters.Druk CV vooralarm | Druk CV vooralarm | MSV Mapper | (33) 001.PT-01A1- | 001 | pt | a | Druk CV vooralarm | Press CV pre-alarm | Boiler | Ketel 1 | Boiler 1 | Boiler |  | Pressure transmitter | Pressure_Sensor | Alarm | Alarm | Alarm
57 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.Druk glycol vooralarm | Druk glycol vooralarm | MSV Mapper | (33) 404.PA-01A1- | 404 | pa | a | Druk glycol vooralarm | Pressure glycol pre-alarm | Energy_Storage |  |  |  | Systeemdruk alarm | System pressure alarm | Pressure_Alarm | Alarm | Alarm | Alarm
58 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.EF-A | EF-A | BI Mapper | (33) 201.VA-01A1- | 201 | va | a | Afvoerventilator storing | Exhaust fan failure | AHU | LBK 1 | AHU 1 | AHU | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Alarm | Alarm | Alarm
59 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SF-A | SF-A | BI Mapper | (33) 201.VT-01A1- | 201 | vt | a | Toevoerventilator storing | Supply fan failure | AHU | LBK 1 | AHU 1 | AHU | Ventilator toevoer | Fan supply | Supply_Fan | Alarm | Alarm | Alarm
60 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.EF-A | EF-A | BI Mapper | (33) 202.VA-01A1- | 202 | va | a | Afvoerventilator storing | Exhaust fan failure | AHU | LBK 2 | AHU 2 | AHU | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Alarm | Alarm | Alarm
61 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.SF-A | SF-A | BI Mapper | (33) 202.VT-01A1- | 202 | vt | a | Toevoerventilator storing | Supply fan failure | AHU | LBK 2 | AHU 2 | AHU | Ventilator toevoer | Fan supply | Supply_Fan | Alarm | Alarm | Alarm
62 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Status storing pomp spuien WB | O-Status storing pomp spuien WB | MSV Mapper | (33) 410.BP-01A1- | 410 | bp | a | Status storing bronpomp spuien WB | Status of fault well pump blowdown WB | Energy_Storage |  |  |  | Bronpomp | Well pump | Water_Pump | Alarm | Alarm | Alarm
63 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Storing open sturen spuiklep | O-Storing open sturen spuiklep | MSV Mapper | (33) 410.CV-01A1- | 410 | cv | a | Storing open sturen spuiklep | Fail to open blowdown valve | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Alarm | Alarm | Alarm
64 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Nivo storing KB | O-Nivo storing KB | MSV Mapper | (33) 410.LT-01A1- | 410 | lt | a | Nivo storing KB | Level malfunction KB | Energy_Storage |  |  |  | Nivo meting | Level measurement | Water_Level_Sensor | Alarm | Alarm | Alarm
65 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Storing max tijdsduur vullen | O-Storing max tijdsduur vullen | MSV Mapper | (33) 410.XR-01A1- | 410 | xr | a | Storing max. tijdsduur vullen | Fault max. filling time | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Alarm | Alarm | Alarm
66 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CH1-A1 | CH1-A1 | BI Mapper | (33).905.XA-01A1- | 905 | xa | a | Proceskoeling unit 1 storing urgent | Process cooling unit 1 fault urgent | Server_Room | SER/MER meldingen | MER = Main Equipment Room, SER = Satellite Equipment Room | Server_Room | Storing algemeen | Malfunction general | Fault_Status | Alarm | Alarm | Alarm
67 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Storing max regelafw flow | O-Storing max regelafw flow | MSV Mapper | (33) 410.XR-01A10 | 410 | xr | a | Storing max. regelafwijking flow | Fault max. control deviation flow | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Alarm | Alarm | Alarm
68 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Flow storing KB | O-Flow storing KB | MSV Mapper | (33) 410.XR-01A19 | 410 | xr | a | Flow storing KB ontladen | Flow failure KB discharged | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Alarm | Alarm | Alarm
69 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Sprinkler-A2 | Sprinkler-A2 | BI Mapper | (33) 501.XA-01A2- | 501 | xa | a | Sprinkeler reserve | Sprinkler reserve | Sprinkler |  | Sprinker | Fire_Safety_System | Storing algemeen | Malfunction general | Fault_Status | Alarm | Alarm | Alarm
70 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Parameters.Drukalarm CV | Drukalarm CV | MSV Mapper | (33) 001.PT-01A2- | 001 | pt | a | Drukalarm CV | Pressure alarm CV | Boiler | Ketel 1 | Boiler 1 | Boiler |  | Pressure transmitter | Pressure_Sensor | Alarm | Alarm | Alarm
71 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.Drukalarm glycol | Drukalarm glycol | MSV Mapper | (33) 404.PA-01A2- | 404 | pa | a | Druk glycol alarm | Pressure glycol alarm | Energy_Storage |  |  |  | Systeemdruk alarm | System pressure alarm | Pressure_Alarm | Alarm | Alarm | Alarm
72 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.EF-A-1 | EF-A-1 | BI Mapper | (33) 201.VA-01A2- | 201 | va | a | Afvoerventilator storing | Exhaust fan failure | AHU | LBK 1 | AHU 1 | AHU | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Alarm | Alarm | Alarm
73 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SF-A-1 | SF-A-1 | BI Mapper | (33) 201.VT-01A2- | 201 | vt | a | Toevoerventilator storing | Supply fan failure | AHU | LBK 1 | AHU 1 | AHU | Ventilator toevoer | Fan supply | Supply_Fan | Alarm | Alarm | Alarm
74 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.EF-A-1 | EF-A-1 | BI Mapper | (33) 202.VA-01A2- | 202 | va | a | Afvoerventilator storing | Exhaust fan failure | AHU | LBK 2 | AHU 2 | AHU | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Alarm | Alarm | Alarm
75 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.SF-A-1 | SF-A-1 | BI Mapper | (33) 202.VT-01A2- | 202 | vt | a | Toevoerventilator storing | Supply fan failure | AHU | LBK 2 | AHU 2 | AHU | Ventilator toevoer | Fan supply | Supply_Fan | Alarm | Alarm | Alarm
76 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Status storing pomp spuien KB | O-Status storing pomp spuien KB | MSV Mapper | (33) 410.BP-01A2- | 410 | bp | a | Status storing bronpomp spuien KB | Status well pump blowdown KB | Energy_Storage |  |  |  | Bronpomp | Well pump | Water_Pump | Alarm | Alarm | Alarm
77 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Storing dicht sturen spuiklep | O-Storing dicht sturen spuiklep | MSV Mapper | (33) 410.CV-01A2- | 410 | cv | a | Storing dicht sturen spuiklep | Failure to close blowdown valve | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Alarm | Alarm | Alarm
78 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Nivo onderhoudsmelding KB | O-Nivo onderhoudsmelding KB | MSV Mapper | (33) 410.LT-01A2- | 410 | lt | a | Nivo onderhoudsmelding KB | Level maintenance message KB | Energy_Storage |  |  |  | Nivo meting | Level measurement | Water_Level_Sensor | Alarm | Alarm | Alarm
79 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Stor min druk laden-ontladen | O-Stor min druk laden-ontladen | MSV Mapper | (33) 410.XR-01A2- | 410 | xr | a | Storing min. druk laden-ontladen | Malfunction min. pressure load-unload | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Alarm | Alarm | Alarm
80 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CH1-A2 | CH1-A2 | BI Mapper | (33).905.XA-01A2- | 905 | xa | a | Proceskoeling unit 1 storing niet urgent | Process cooling unit 1 malfunction not urgent | Server_Room | SER/MER meldingen | MER = Main Equipment Room, SER = Satellite Equipment Room | Server_Room | Storing algemeen | Malfunction general | Fault_Status | Alarm | Alarm | Alarm
81 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Storing afschakelen ontladen | O-Storing afschakelen ontladen | MSV Mapper | (33) 410.XR-01A21 | 410 | xr | a | Storing afschakelen ontladen | Fault shutdown unload | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Alarm | Alarm | Alarm
82 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Flow storing WB laden | O-Flow storing WB laden | MSV Mapper | (33) 410.XR-01A22 | 410 | xr | a | Flow storing WB laden | Flow failure WB load | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Alarm | Alarm | Alarm
83 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Flow storing WB spuien | O-Flow storing WB spuien | MSV Mapper | (33) 410.XR-01A23 | 410 | xr | a | Flow storing WB of KB spuien | Flow failure WB or KB blowdown | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Alarm | Alarm | Alarm
84 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Datum onderhoudsmelding KB | O-Datum onderhoudsmelding KB | MSV Mapper | (33) 410.XR-01A24 | 410 | xr | a | Datum onderhoudsmelding KB | Date maintenance notification KB | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Alarm | Alarm | Alarm
85 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Datum onderhoudsmelding WB | O-Datum onderhoudsmelding WB | MSV Mapper | (33) 410.XR-01A25 | 410 | xr | a | Datum onderhoudsmelding WB | Date maintenance notification WB | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Alarm | Alarm | Alarm
86 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Verzamelstoring urgent | O-Verzamelstoring urgent | MSV Mapper | (33) 410.XR-01A26 | 410 | xr | a | Verzamelstoring urgent | Collective fault urgent | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Alarm | Alarm | Alarm
87 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Sprinkler-A3 | Sprinkler-A3 | BI Mapper | (33) 501.XA-01A3- | 501 | xa | a | Sprinkeler reserve | Sprinkler reserve | Sprinkler |  | Sprinker | Fire_Safety_System | Storing algemeen | Malfunction general | Fault_Status | Alarm | Alarm | Alarm
88 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Nivo storing KB spuien | O-Nivo storing KB spuien | MSV Mapper | (33) 410.LT-01A3- | 410 | lt | a | Nivo storing KB spuien | Level failure KB flushing | Energy_Storage |  |  |  | Nivo meting | Level measurement | Water_Level_Sensor | Alarm | Alarm | Alarm
89 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Bron systeem ontluchten | O-Bron systeem ontluchten | MSV Mapper | (33) 410.XR-01A3- | 410 | xr | a | Bron systeem ontluchten | Bleed source system | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Alarm | Alarm | Alarm
90 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Storing maximum druk | O-Storing maximum druk | MSV Mapper | (33) 410.XR-01A4- | 410 | xr | a | Storing maximum druk | Maximum pressure fault | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Alarm | Alarm | Alarm
91 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Storing afschakelen laden | O-Storing afschakelen laden | MSV Mapper | (33) 410.XR-01A5- | 410 | xr | a | Storing afschakelen laden | Disable loading fault | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Alarm | Alarm | Alarm
92 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Storing drukhandhaving te vaak | O-Storing drukhandhaving te vaak | MSV Mapper | (33) 410.XR-01A6- | 410 | xr | a | Storing drukhandhaving te vaak | Pressure maintenance failure too frequent | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Alarm | Alarm | Alarm
93 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Storing drukhandhaving te lang | O-Storing drukhandhaving te lang | MSV Mapper | (33) 410.XR-01A9- | 410 | xr | a | Storing drukhandhaving te lang | Pressure hold fault too long | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Alarm | Alarm | Alarm
94 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.MISC3-A | MISC3-A | BI Mapper | (33) 801.RK-01AI- | 801 | rk | ai | Installatie automaten | Installation machines | Breaker_Panel | Schakelkast RK-01 | Electricity Control cabinet RK-01 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel | installatie automaten | Fuse | Switchgear
95 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.INST-A | INST-A | BI Mapper | (33) 802.RK-01AI- | 802 | rk | ai | Installatieautomaten | Automatic circuit breakers | Breaker_Panel | Schakelkast RK-02 | Electricity Control cabinet RK-02 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel | installatie automaten | Fuse | Switchgear
96 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Installatie automaten | Installatie automaten | BI Mapper | (33) 803.RK-01AI- | 803 | rk | ai | Installatie automaten | Installation machines | Breaker_Panel |  |  |  | Regelkast | Control box, Switch box | Breaker_Panel | installatie automaten | Fuse | Switchgear
97 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.MISC1-A | MISC1-A | BI Mapper | (33) 801.RK-01AN- | 801 | rk | an | Netwachter | Netkeeper | Breaker_Panel | Schakelkast RK-01 | Electricity Control cabinet RK-01 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel | netwachter | Power phase monitor (alarm) | Power_Loss_Alarm
98 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.NETW-A-1 | NETW-A-1 | BI Mapper | (33) 802.RK-01AN- | 802 | rk | an | Netwachter | Netkeeper | Breaker_Panel | Schakelkast RK-02 | Electricity Control cabinet RK-02 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel | netwachter | Power phase monitor (alarm) | Power_Loss_Alarm
99 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Netwachter | Netwachter | BI Mapper | (33) 803.RK-01AN- | 803 | rk | an | Netwachter | Netkeeper | Breaker_Panel |  |  |  | Regelkast | Control box, Switch box | Breaker_Panel | netwachter | Power phase monitor (alarm) | Power_Loss_Alarm
100 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SHWP1-S | SHWP1-S | BI Mapper | (33) 001.TP-01B-- | 001 | tp | b | Transportpomp 1 bedrijf | Transport pump 1 operation | Boiler | Ketel 1 | Boiler 1 | Boiler | Transportpomp | Transport pump | Pump | Bedrijfsmelding | Operation status | Status
101 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.MISC-S1 | MISC-S1 | BI Mapper | (33) 902.LV-01B-- | 902 | lv | b | Tracing vetvangleiding groep 1 bedrijf | Tracing grease trap line group 1 company | [5 empty] | Tracing grease trap line |  | Bedrijfsmelding | Operation status | Status
102 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.HCP-S | HCP-S | BI Mapper | (33) 021.CP-01B-- | 021 | cp | b | Circulatiepomp bedrijf | Circulation pump operation | Hot_Water_System | Warm water groep 1 | Hot water group 1 | Hot_Water_System | Circulatie pomp | Circulation pump | Pump | Bedrijfsmelding | Operation status | Status
103 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.HCP-S | HCP-S | BI Mapper | (33) 022.CP-01B-- | 022 | cp | b | Circulatiepomp bedrijf | Circulation pump operation | Hot_Water_System | Warm water groep 2 | Hot water group 2 | Hot_Water_System | Circulatie pomp | Circulation pump | Pump | Bedrijfsmelding | Operation status | Status
104 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWP-S | SCHWP-S | BI Mapper | (33) 121.CP-01B-- | 121 | cp | b | Circulatiepomp bedrijf | Circulation pump operation | Chilled_Water_System | Gekoeld water groep 1 | Chilled water group 1 | Chilled_Water_System | Circulatie pomp | Circulation pump | Pump | Bedrijfsmelding | Operation status | Status
105 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWP1-S | SCHWP1-S | BI Mapper | (33) 122.TP-01B-- | 122 | tp | b | Transportpomp 1 bedrijf | Transport pump 1 operation | Chilled_Water_System | Gekoeld water groep 2 | Chilled water group 2 | Chilled_Water_System | Transportpomp | Transport pump | Pump | Bedrijfsmelding | Operation status | Status
106 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CH1-S | CH1-S | BI Mapper | (33) 403.WP-01B-- | 403 | wp | b | Warmtepomp bedrijf | Heat pump company | Energy_Storage |  |  |  | Warmtepomp | Heat pump | Equipment | Bedrijfsmelding | Operation status | Status
107 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CWP1-S | CWP1-S | BI Mapper | (33) 403.CP-01B-- | 403 | cp | b | Circulatiepomp WP-CV bedrijf | Circulation pump WP-CV operation | Energy_Storage |  |  |  | Circulatie pomp | Circulation pump | Pump | Bedrijfsmelding | Operation status | Status
108 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.TP-S | TP-S | BI Mapper | (33) 402.TP-01B-- | 402 | tp | b | Transportpomp bronnen bedrijf | Conveyor pump sources company | Energy_Storage | Koudebron | Cold source | Energy_Storage | Transportpomp | Transport pump | Pump | Bedrijfsmelding | Operation status | Status
109 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CWP1-S | CWP1-S | BI Mapper | (33) 404.CP-01B-- | 404 | cp | b | Circulatiepomp drogekoeler prim. bedrijf | Circulation pump dry cooler prim. company | Energy_Storage |  |  |  | Circulatie pomp | Circulation pump | Pump | Bedrijfsmelding | Operation status | Status
110 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CT1-S | CT1-S | BI Mapper | (33) 404.DK-01B-- | 404 | dk | b | Drogekoeler bedrijf | Dry cooler company | Energy_Storage |  |  |  | Doseer klep | Dosing valve | Valve | Bedrijfsmelding | Operation status | Status
111 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.301-HS-S-1 | 301-HS-S-1 | BI Mapper | (33) 301.HS-01B-- | 301 | hs | b | Handschakelaar uit/aan | Hand switch off/on | Exhaust_Fan | Afzuig liftmachinekamer | Exhaust fan for machine room of elevator | Exhaust_Fan |  | Switch (manual) | Switch | Bedrijfsmelding | Operation status | Status
112 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.302-AV1-B | 302-AV1-B | BI Mapper | (33) 302.VA-01B-- | 302 | va | b | Afzuigventilator containerruimte bedr | Exhaust fan container room oper | Exhaust_Fan | Afzuig toiletten | Exhaust fan for toilets | Exhaust_Fan | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Bedrijfsmelding | Operation status | Status
113 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.301-AV1-B | 301-AV1-B | BI Mapper | (33) 301.VA-01B-- | 301 | va | b | Afzuigventilator horeca links bedrijf | Exhaust fan catering left company | Exhaust_Fan | Afzuig liftmachinekamer | Exhaust fan for machine room of elevator | Exhaust_Fan | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Bedrijfsmelding | Operation status | Status
114 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.202-SA-S | 202-SA-S | BI Mapper | (33) 201.XS-01B-- | 201 | xs | b | LBK 202 in bedrijf stand-alone | LBK 202 in stand-alone operation | AHU | LBK 1 | AHU 1 | AHU | Status algemeen | General status | Status | Bedrijfsmelding | Operation status | Status
115 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.PHP-S | PHP-S | BI Mapper | (33) 201.CP-01B-- | 201 | cp | b | Circulatiepomp bedrijf | Circulation pump operation | AHU | LBK 1 | AHU 1 | AHU | Circulatie pomp | Circulation pump | Pump | Bedrijfsmelding | Operation status | Status
116 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.HRW-S | HRW-S | BI Mapper | (33) 201.WW-01B-- | 201 | ww | b | Warmtewiel bedrijf | Heat wheel company | AHU | LBK 1 | AHU 1 | AHU | Warmtewiel | Rotary heat recovery | Heat_Wheel | Bedrijfsmelding | Operation status | Status
117 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.202-SA-S | 202-SA-S | BI Mapper | (33) 202.XS-01B-- | 202 | xs | b | LBK 202 in bedrijf stand-alone | LBK 202 in stand-alone operation | AHU | LBK 2 | AHU 2 | AHU | Status algemeen | General status | Status | Bedrijfsmelding | Operation status | Status
118 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.PHP-S | PHP-S | BI Mapper | (33) 202.CP-01B-- | 202 | cp | b | Circulatiepomp bedrijf | Circulation pump operation | AHU | LBK 2 | AHU 2 | AHU | Circulatie pomp | Circulation pump | Pump | Bedrijfsmelding | Operation status | Status
119 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.HRW-S | HRW-S | BI Mapper | (33) 202.WW-01B-- | 202 | ww | b | Warmtewiel bedrijf | Heat wheel company | AHU | LBK 2 | AHU 2 | AHU | Warmtewiel | Rotary heat recovery | Heat_Wheel | Bedrijfsmelding | Operation status | Status
120 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Werkschakelaar warmebron | Werkschakelaar warmebron | BI Mapper | (33) 411.HS-01B-- | 411 | hs | b | Werkschakelaar warmebron | Work switch heat source | Energy_Storage |  |  |  |  | Switch (manual) | Switch | Bedrijfsmelding | Operation status | Status
121 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Werkschakelaar koudebron | Werkschakelaar koudebron | BI Mapper | (33) 412.HS-01B-- | 412 | hs | b | Werkschakelaar koudebron | Work switch cold source | Energy_Storage |  |  |  |  | Switch (manual) | Switch | Bedrijfsmelding | Operation status | Status
122 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Puls drukker start spuien | Puls drukker start spuien | BI Mapper | (33) 413.HS-01B-- | 413 | hs | b | Puls drukker start spuien | Pulse pusher starts blowdown | Energy_Storage |  |  |  |  | Switch (manual) | Switch | Bedrijfsmelding | Operation status | Status
123 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.HXCWP1-S | HXCWP1-S | BI Mapper | (33) 903.HYD01B-- | 903 | hyd | b | Hydrofoor bedrijf | Hydrophore company |  |  |  |  | Hydrofoor installatie | Pressurized water installation Hydrophore installation to maintain water pressure |  | Bedrijfsmelding | Operation status | Status
124 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC011.OCC-S | OCC-S | BI Mapper | (33-0) 711.PIR01B-- | 711 | pir | b | Aanwezigheid | Presence | Equipment |  |  |  | Passief infrarood | Passive infrared PIR | PIR_Sensor | Bedrijfsmelding | Operation status | Status
125 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC013.OCC-S | OCC-S | BI Mapper | (33-0) 713.PIR01B-- | 713 | pir | b | Aanwezigheid | Presence | Equipment |  |  |  | Passief infrarood | Passive infrared PIR | PIR_Sensor | Bedrijfsmelding | Operation status | Status
126 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.OCC-S | OCC-S | BI Mapper | (33-1) 719.PIR01B-- | 719 | pir | b | Aanwezigheid | Presence | Equipment |  |  |  | Passief infrarood | Passive infrared PIR | PIR_Sensor | Bedrijfsmelding | Operation status | Status
127 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC020.OCC-S | OCC-S | BI Mapper | (33-1) 720.PIR01B-- | 720 | pir | b | Aanwezigheid | Presence | Equipment |  |  |  | Passief infrarood | Passive infrared PIR | PIR_Sensor | Bedrijfsmelding | Operation status | Status
128 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC022.OCC-S | OCC-S | BI Mapper | (33-1) 722.PIR01B-- | 722 | pir | b | Aanwezigheid | Presence | Equipment |  |  |  | Passief infrarood | Passive infrared PIR | PIR_Sensor | Bedrijfsmelding | Operation status | Status
129 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.OCC-S | OCC-S | BI Mapper | (33-1) 723.PIR01B-- | 723 | pir | b | Aanwezigheid | Presence | Equipment |  |  |  | Passief infrarood | Passive infrared PIR | PIR_Sensor | Bedrijfsmelding | Operation status | Status
130 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC024.OCC-S | OCC-S | BI Mapper | (33-2) 724.PIR01B-- | 724 | pir | b | Aanwezigheid | Presence | Equipment |  |  |  | Passief infrarood | Passive infrared PIR | PIR_Sensor | Bedrijfsmelding | Operation status | Status
131 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC025.OCC-S | OCC-S | BI Mapper | (33-2) 725.PIR01B-- | 725 | pir | b | Aanwezigheid | Presence | Equipment |  |  |  | Passief infrarood | Passive infrared PIR | PIR_Sensor | Bedrijfsmelding | Operation status | Status
132 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC027.OCC-S | OCC-S | BI Mapper | (33-2) 727.PIR01B-- | 727 | pir | b | Aanwezigheid | Presence | Equipment |  |  |  | Passief infrarood | Passive infrared PIR | PIR_Sensor | Bedrijfsmelding | Operation status | Status
133 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC028.OCC-S | OCC-S | BI Mapper | (33-2) 728.PIR01B-- | 728 | pir | b | Aanwezigheid | Presence | Equipment |  |  |  | Passief infrarood | Passive infrared PIR | PIR_Sensor | Bedrijfsmelding | Operation status | Status
134 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC029.OCC-S | OCC-S | BI Mapper | (33-2) 729.PIR01B-- | 729 | pir | b | Aanwezigheid | Presence | Equipment |  |  |  | Passief infrarood | Passive infrared PIR | PIR_Sensor | Bedrijfsmelding | Operation status | Status
135 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC031.OCC-S | OCC-S | BI Mapper | (33-2) 731.PIR01B-- | 731 | pir | b | Aanwezigheid | Presence | Equipment |  |  |  | Passief infrarood | Passive infrared PIR | PIR_Sensor | Bedrijfsmelding | Operation status | Status
136 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SF-S | SF-S | BI Mapper | (33) 201.VT-01B1- | 201 | vt | b | Toevoerventilator bedrijf | Supply fan operation | AHU | LBK 1 | AHU 1 | AHU | Ventilator toevoer | Fan supply | Supply_Fan | Bedrijfsmelding | Operation status | Status
137 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.EF-S | EF-S | BI Mapper | (33) 201.VA-01B1- | 201 | va | b | Afvoerventilator bedrijf | Exhaust fan operation | AHU | LBK 1 | AHU 1 | AHU | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Bedrijfsmelding | Operation status | Status
138 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.SF-S | SF-S | BI Mapper | (33) 202.VT-01B1- | 202 | vt | b | Toevoerventilator bedrijf | Supply fan operation | AHU | LBK 2 | AHU 2 | AHU | Ventilator toevoer | Fan supply | Supply_Fan | Bedrijfsmelding | Operation status | Status
139 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.EF-S | EF-S | BI Mapper | (33) 202.VA-01B1- | 202 | va | b | Afvoerventilator bedrijf | Exhaust fan operation | AHU | LBK 2 | AHU 2 | AHU | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Bedrijfsmelding | Operation status | Status
140 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SF-S-1 | SF-S-1 | BI Mapper | (33) 201.VT-01B2- | 201 | vt | b | Toevoerventilator bedrijf | Supply fan operation | AHU | LBK 1 | AHU 1 | AHU | Ventilator toevoer | Fan supply | Supply_Fan | Bedrijfsmelding | Operation status | Status
141 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.EF-S-1 | EF-S-1 | BI Mapper | (33) 201.VA-01B2 | 201 | va | b | Afvoerventilator bedrijf | Exhaust fan operation | AHU | LBK 1 | AHU 1 | AHU | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Bedrijfsmelding | Operation status | Status
142 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.SF-S-1 | SF-S-1 | BI Mapper | (33) 202.VT-01B2- | 202 | vt | b | Toevoerventilator bedrijf | Supply fan operation | AHU | LBK 2 | AHU 2 | AHU | Ventilator toevoer | Fan supply | Supply_Fan | Bedrijfsmelding | Operation status | Status
143 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.EF-S-1 | EF-S-1 | BI Mapper | (33) 202.VA-01B2 | 202 | va | b | Afvoerventilator bedrijf | Exhaust fan operation | AHU | LBK 2 | AHU 2 | AHU | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Bedrijfsmelding | Operation status | Status
144 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.FIRE-A | FIRE-A | BI Mapper | (33) 801.RK-01BA- | 801 | rk | ba | Brandmelding | Fire alarm | Breaker_Panel | Schakelkast RK-01 | Electricity Control cabinet RK-01 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel
145 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.FCP-A | FCP-A | BI Mapper | (33) 802.RK-01BA- | 802 | rk | ba | Brandmelding | Fire alarm | Breaker_Panel | Schakelkast RK-02 | Electricity Control cabinet RK-02 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel
146 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Brandmelding | Brandmelding | BI Mapper | (33) 803.RK-01BA- | 803 | rk | ba | Brandmelding | Fire alarm | Breaker_Panel |  |  |  | Regelkast | Control box, Switch box | Breaker_Panel
147 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.FIRE-C | FIRE-C | BO Mapper | (33) 801.RK-01BMC | 801 | rk | bmc | Brandlamp | Fire lamp | Breaker_Panel | Schakelkast RK-01 | Electricity Control cabinet RK-01 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel
148 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.BA-C | BA-C | BO Mapper | (33) 802.RK-01BMC | 802 | rk | bmc | Brandlamp | Fire lamp | Breaker_Panel | Schakelkast RK-02 | Electricity Control cabinet RK-02 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel
149 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Brandlamp | Brandlamp | BO Mapper | (33) 803.RK-01BMC | 803 | rk | bmc | Brandlamp | Fire lamp | Breaker_Panel |  |  |  | Regelkast | Control box, Switch box | Breaker_Panel
150 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.PHWL-T | PHWL-T | AI Mapper | (33) 001.TT-01M-- | 001 | tt | m | Aanvoertemperatuur CV | CH flow temperature | Boiler | Ketel 1 | Boiler 1 | Boiler | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
151 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.MISC-P | MISC-P | AI Mapper | (33) 001.PT-01M-- | 001 | pt | m | Systeemdrukopnemer | System pressure sensor | Boiler | Ketel 1 | Boiler 1 | Boiler |  | Pressure transmitter | Pressure_Sensor | Meting | Measurement | Sensor
152 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.MISCE-T | MISCE-T | AI Mapper | (33) 021.TT-01M-- | 021 | tt | m | Aanvoertemperatuur | Supply temperature | Hot_Water_System | Warm water groep 1 | Hot water group 1 | Hot_Water_System | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
153 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.MISCE-T | MISCE-T | AI Mapper | (33) 022.TT-01M-- | 022 | tt | m | Aanvoertemperatuur | Supply temperature | Hot_Water_System | Warm water groep 2 | Hot water group 2 | Hot_Water_System | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
154 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.MISC-T | MISC-T | AI Mapper | (33) 041.TT-01M-- | 041 | tt | m | Koudtapwater temperatuur | Cold tap water temperature | Hot_Water_System |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
155 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.MISC-P | MISC-P | AI Mapper | (33) 122.PT-01M-- | 122 | pt | m | Systeemdrukopnemer | System pressure sensor | Chilled_Water_System | Gekoeld water groep 2 | Chilled water group 2 | Chilled_Water_System |  | Pressure transmitter | Pressure_Sensor | Meting | Measurement | Sensor
156 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.PCHWL2-T | PCHWL2-T | AI Mapper | (33) 122.TT-01M-- | 122 | tt | m | Aanvoertemperatuur | Supply temperature | Chilled_Water_System | Gekoeld water groep 2 | Chilled water group 2 | Chilled_Water_System | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
157 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.PCHWL1-T | PCHWL1-T | AI Mapper | (33) 121.TT-01M-- | 121 | tt | m | Aanvoertemperatuur | Supply temperature | Chilled_Water_System | Gekoeld water groep 1 | Chilled water group 1 | Chilled_Water_System | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
158 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CHWE2-T | CHWE2-T | AI Mapper | (33) 124.TT-01M-- | 124 | tt | m | Retourtemperatuur proceskoeling SER 2 | Return temperature process cooling SER 2 | Chilled_Water_System |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
159 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CHWE1-T | CHWE1-T | AI Mapper | (33) 123.TT-01M-- | 123 | tt | m | Retourtemperatuur proceskoeling SER 1 | Return temperature process cooling SER 1 | Chilled_Water_System |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
160 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CHW-F | CHW-F | AI Mapper | (33) 402.FT-01M-- | 402 | ft | m | Flowmeter laden/ontladen | Charge/discharge flow meter | Energy_Storage | Koudebron | Cold source | Energy_Storage | Flow transmitter | flow transmitter | Water_Meter | Meting | Measurement | Sensor
161 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CHWL1-T | CHWL1-T | AI Mapper | (33) 402.TT-01M-- | 402 | tt | m | Aanvoertemperatuur bronnen | Supply temperature sources | Energy_Storage | Koudebron | Cold source | Energy_Storage | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
162 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CH1CWS-T | CH1CWS-T | AI Mapper | (33) 403.TT-01M-- | 403 | tt | m | Aanvoertemperatuur WP-CV | Supply temperature WP-CV | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
163 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CT1-DO% | CT1-DO% | AI Mapper | (33) 404.DK-01M-- | 404 | dk | m | Uitlezing drogekoeler | Dry cooler readout | Energy_Storage |  |  |  | Doseer klep | Dosing valve | Valve | Meting | Measurement | Sensor
164 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CWR2-T | CWR2-T | AI Mapper | (33) 404.TT-01M-- | 404 | tt | m | Aanvoertemperatuur prim. | Supply temperature prim. | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
165 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.MISC-P | MISC-P | AI Mapper | (33) 404.PT-01M-- | 404 | pt | m | Systeemdrukopnemer | System pressure sensor | Energy_Storage |  |  |  |  | Pressure transmitter | Pressure_Sensor | Meting | Measurement | Sensor
166 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.203-DA-T | 203-DA-T | AI Mapper | (33) 203.TT-01M-- | 203 | tt | m | Inblaasluchttemperatuur LBK1 en LBK2 | Supply air temperature AHU1 and AHU2 | AHU |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
167 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.301-EF-RPM-1 | 301-EF-RPM-1 | AI Mapper | (33) 301.VA-01M-- | 301 | va | m | Afzuigventilator horeca links terugkop. | Extractor fan catering left back. | Exhaust_Fan | Afzuig liftmachinekamer | Exhaust fan for machine room of elevator | Exhaust_Fan | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Meting | Measurement | Sensor
168 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.203-DA-Q | 203-DA-Q | AI Mapper | (33) 203.QT-01M-- | 203 | qt | m | Inblaasluchtkwaliteit LBK1 en LBK2 | Supply air quality AHU1 and AHU2 | AHU |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
169 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.203-DA-H | 203-DA-H | AI Mapper | (33) 203.MT-01M-- | 203 | mt | m | Inblaasluchtvochtigheid LBK1 en LBK2 | Inlet air humidity LBK 1 and LBK2 | AHU |  |  |  | Vocht transmitter | Moisture transmitter | Humidity_Sensor | Meting | Measurement | Sensor
170 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.DA-H | DA-H | AI Mapper | (33) 201.MT-01M-- | 201 | mt | m | Inblaasluchtvochtigheid | Inlet air humidity | AHU | LBK 1 | AHU 1 | AHU | Vocht transmitter | Moisture transmitter | Humidity_Sensor | Meting | Measurement | Sensor
171 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.DA-T | DA-T | AI Mapper | (33) 201.TT-01M-- | 201 | tt | m | Inblaasluchttemperatuur | Supply air temperature | AHU | LBK 1 | AHU 1 | AHU | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
172 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.DA-P | DA-P | AI Mapper | (33) 201.PT-01M-- | 201 | pt | m | Inblaasdruk | Inlet pressure | AHU | LBK 1 | AHU 1 | AHU |  | Pressure transmitter | Pressure_Sensor | Meting | Measurement | Sensor
173 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.DA-H | DA-H | AI Mapper | (33) 202.MT-01M-- | 202 | mt | m | Inblaasluchtvochtigheid | Inlet air humidity | AHU | LBK 2 | AHU 2 | AHU | Vocht transmitter | Moisture transmitter | Humidity_Sensor | Meting | Measurement | Sensor
174 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.DA-T | DA-T | AI Mapper | (33) 202.TT-01M-- | 202 | tt | m | Inblaasluchttemperatuur | Supply air temperature | AHU | LBK 2 | AHU 2 | AHU | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
175 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.DA-P | DA-P | AI Mapper | (33) 202.PT-01M-- | 202 | pt | m | Inblaasdruk | Inlet pressure | AHU | LBK 2 | AHU 2 | AHU |  | Pressure transmitter | Pressure_Sensor | Meting | Measurement | Sensor
176 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC014.ZN1-T | ZN1-T | AI Mapper | (33-0) 714.TT-01M-- | 714 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
177 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC016.DA-T | DA-T | AI Mapper | (33-0) 716.TT-01M-- | 716 | tt | m | Inblaastemperatuur | Inlet temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
178 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC017.DA-T | DA-T | AI Mapper | (33-0) 717.TT-01M-- | 717 | tt | m | Inblaastemperatuur | Inlet temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
179 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC018.DA-T | DA-T | AI Mapper | (33-0) 718.TT-01M-- | 718 | tt | m | Inblaastemperatuur | Inlet temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
180 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC011.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-0) 711.QT-01M-- | 711 | qt | m | Luchthoeveelheid | Air quantity | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
181 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC012.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-0) 712.QT-01M-- | 712 | qt | m | Luchthoeveelheid | Air quantity | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
182 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC013.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-0) 713.QT-01M-- | 713 | qt | m | Flow berekening TV1 | Flow calculation TV1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
183 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC015.Network Outputs.O-AV1-O | O-AV1-O | AV Mapper | (33-0) 715.QT-01M-- | 715 | qt | m | Luchthoeveelheid | Air quantity | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
184 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC016.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-0) 716.QT-01M-- | 716 | qt | m | Luchthoeveelheid | Air quantity | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
185 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC017.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-0) 712.QT-01M-- | 712 | qt | m | Flow berekening TV1 | Flow calculation TV1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
186 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC018.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-0) 718.QT-01M-- | 718 | qt | m | Luchthoeveelheid | Air quantity | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
187 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-1) 719.QT-01M-- | 719 | qt | m | Luchthoeveelheid | Air quantity | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
188 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC020.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-1) 720.QT-01M-- | 720 | qt | m | luchthoeveelheid | air volume | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
189 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC021.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-1) 721.QT-01M-- | 721 | qt | m | Flow berekening TV1 | Flow calculation TV1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
190 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC022.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-1) 722.QT-01M-- | 722 | qt | m | Flow berekening TV1 | Flow calculation TV1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
191 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-1) 723.QT-01M-- | 723 | qt | m | Flow berekening TV1 | Flow calculation TV1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
192 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC024.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-2) 724.QT-01M-- | 724 | qt | m | Flow berekening TV1 | Flow calculation TV1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
193 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC025.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-2) 725.QT-01M-- | 725 | qt | m | Luchthoeveelheid | Air quantity | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
194 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC026.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-2) 726.QT-01M-- | 726 | qt | m | Flow berekening TV1 | Flow calculation TV1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
195 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC027.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-2) 727.QT-01M-- | 727 | qt | m | Flow berekening TV1 | Flow calculation TV1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
196 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC028.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-2) 728.QT-01M-- | 728 | qt | m | Flow berekening TV1 | Flow calculation TV1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
197 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC029.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-2) 729.QT-01M-- | 729 | qt | m | Flow berekening TV1 | Flow calculation TV1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
198 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC030.Network Outputs.O-AV1-O | O-AV1-O | AV Mapper | (33-2) 730.QT-01M-- | 730 | qt | m | Flow berekening V1 | Flow calculation V1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
199 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC031.Network Outputs.O-TV1-O | O-TV1-O | AV Mapper | (33-2) 731.QT-01M-- | 731 | qt | m | Flow berekening TV1 | Flow calculation TV1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
200 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Aanvoertemp koude bron | Aanvoertemp koude bron | AI Mapper | (33) 412.TT-01M-- | 412 | tt | m | Aanvoertemp koude bron | Cold source flow temp | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
201 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Aanvoertemp warme bron | Aanvoertemp warme bron | AI Mapper | (33) 411.TT-01M-- | 411 | tt | m | Aanvoertemp warme bron | Hot source flow temp | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
202 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Flowmeting primair TSA | Flowmeting primair TSA | AI Mapper | (33) 410.FT-01M-- | 410 | ft | m | Flowmeting primair TSA | Flow measurement primary TSA | Energy_Storage |  |  |  | Flow transmitter | flow transmitter | Water_Meter | Meting | Measurement | Sensor
203 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Systeem druk primair TSA | Systeem druk primair TSA | AI Mapper | (33) 410.PT-01M-- | 410 | pt | m | Systeem druk primair TSA | System pressure primary TSA | Energy_Storage |  |  |  |  | Pressure transmitter | Pressure_Sensor | Meting | Measurement | Sensor
204 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Niveau warme bron | Niveau warme bron | AI Mapper | (33) 411.LT-01M-- | 411 | lt | m | Niveau warme bron | Hot source level | Energy_Storage |  |  |  | Nivo meting | Level measurement | Water_Level_Sensor | Meting | Measurement | Sensor
205 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Systeem druk warme bron | Systeem druk warme bron | AI Mapper | (33) 411.PT-01M-- | 411 | pt | m | Systeem druk warme bron | System pressure hot source | Energy_Storage |  |  |  |  | Pressure transmitter | Pressure_Sensor | Meting | Measurement | Sensor
206 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Niveau koude bron | Niveau koude bron | AI Mapper | (33) 412.LT-01M-- | 412 | lt | m | Niveau koude bron | Cold well level | Energy_Storage |  |  |  | Nivo meting | Level measurement | Water_Level_Sensor | Meting | Measurement | Sensor
207 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Systeem druk koude bron | Systeem druk koude bron | AI Mapper | (33) 412.PT-01M-- | 412 | pt | m | Systeem druk koude bron | System pressure cold source | Energy_Storage |  |  |  |  | Pressure transmitter | Pressure_Sensor | Meting | Measurement | Sensor
208 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.HW-DP | HW-DP | AI Mapper | (33) 001.PdT01M-- | 001 | pdt | m | Drukverschilopnemer | Differential pressure sensor | Boiler | Ketel 1 | Boiler 1 | Boiler | Drukverschil meting | Differential pressure measurement | Differential_Pressure_Sensor | Meting | Measurement | Sensor
209 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CHW-DP | CHW-DP | AI Mapper | (33) 122.PdT01M-- | 122 | pdt | m | Drukverschilopnemer | Differential pressure sensor | Chilled_Water_System | Gekoeld water groep 2 | Chilled water group 2 | Chilled_Water_System | Drukverschil meting | Differential pressure measurement | Differential_Pressure_Sensor | Meting | Measurement | Sensor
210 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.PFILT-DP | PFILT-DP | AI Mapper | (33) 201.PDT01M-- | 201 | pdt | m | Drukverschil toevoerfilter | Pressure differential supply filter | AHU | LBK 1 | AHU 1 | AHU | Drukverschil meting | Differential pressure measurement | Differential_Pressure_Sensor | Meting | Measurement | Sensor
211 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.PFILT-DP | PFILT-DP | AI Mapper | (33) 202.PDT01M-- | 202 | pdt | m | Drukverschil toevoerfilter | Pressure differential supply filter | AHU | LBK 2 | AHU 2 | AHU | Drukverschil meting | Differential pressure measurement | Differential_Pressure_Sensor | Meting | Measurement | Sensor
212 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Verschil stijghoogte WB | O-Verschil stijghoogte WB | AV Mapper | (33) 410.XR-01M13 | 410 | xr | m | Verschil stijghoogte WB | Difference ascent height WB | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Meting | Measurement | Sensor
213 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Rust nivo WB | O-Rust nivo WB | AV Mapper | (33) 410.XR-01M15 | 410 | xr | m | Rust nivo WB | Rest level WB | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Meting | Measurement | Sensor
214 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Rust nivo KB | O-Rust nivo KB | AV Mapper | (33) 410.XR-01M17 | 410 | xr | m | Rust nivo KB | Rest level KB | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Meting | Measurement | Sensor
215 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Verschil stijghoogte KB | O-Verschil stijghoogte KB | AV Mapper | (33) 410.XR-01M20 | 410 | xr | m | Verschil stijghoogte KB | Difference in height KB | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Meting | Measurement | Sensor
216 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SM1-OP | SM1-OP | BI Mapper | (33) 402.CV-01O-- | 402 | cv | o | Wisselklep bronnen open | Diverter valve sources open | Energy_Storage | Koudebron | Cold source | Energy_Storage | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
217 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM1-OP | SM1-OP | BI Mapper | (33) 404.CV-01O-- | 404 | cv | o | Wisselklep drogekoeler open | Drycooler diverter valve open | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
218 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.BK-01-O | BK-01-O | BI Mapper | (33) 203.BK-01O--(reserve) | 203 | bk | o | Brandkleppen open bgg | Fire dampers open bgg | AHU |  |  |  |  | Firedamper | Damper | Open | Open | Open_Close_Status
219 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.OAD-O | OAD-O | BI Mapper | (33) 201.CD-01O-- | 201 | cd | o | Aanzuigluchtklep open | Suction air valve open | AHU | LBK 1 | AHU 1 | AHU | Luchtklep | Air valve | Gas_Valve | Open | Open | Open_Close_Status
220 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.OAD-O | OAD-O | BI Mapper | (33) 202.CD-01O-- | 202 | cd | o | Aanzuigluchtklep open | Suction air valve open | AHU | LBK 2 | AHU 2 | AHU | Luchtklep | Air valve | Gas_Valve | Open | Open | Open_Close_Status
221 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Spuiklep riool status open | Spuiklep riool status open | BI Mapper | (33) 413.CV-01O-- | 413 | cv | o | Spuiklep riool status open | Drain valve sewer status open | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
222 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.MISC2-A | MISC2-A | BI Mapper | (33) 801.RK-01OB- | 801 | rk | ob | Overspanningsbeveiliging | Overvoltage protection | Breaker_Panel | Schakelkast RK-01 | Electricity Control cabinet RK-01 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel
223 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.OV-A-2 | OV-A-2 | BI Mapper | (33) 802.RK-01OB- | 802 | rk | ob | Overspanningsbeveiliging | Overvoltage protection | Breaker_Panel | Schakelkast RK-02 | Electricity Control cabinet RK-02 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel
224 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Overspanningsbeveiliging | Overspanningsbeveiliging | BI Mapper | (33) 803.RK-01OB- | 803 | rk | ob | Overspanningsbeveiliging | Overvoltage protection | Breaker_Panel |  |  |  | Regelkast | Control box, Switch box | Breaker_Panel
225 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.MISC-C1 | MISC-C1 | BO Mapper | (33) 902.LV-01S-- | 902 | lv | s | Tracing vetvangleiding groep 1 vrijgave | Tracing grease trap line group 1 release | [5 empty] | Tracing grease trap line |  | Schakelen | Switch | Status
226 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.HCP-C | HCP-C | BO Mapper | (33) 021.CP-01S-- | 021 | cp | s | Circulatiepomp vrijgave | Circulation pump release | Hot_Water_System | Warm water groep 1 | Hot water group 1 | Hot_Water_System | Circulatie pomp | Circulation pump | Pump | Schakelen | Switch | Status
227 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.HCP-C | HCP-C | BO Mapper | (33) 022.CP-01S-- | 022 | cp | s | Circulatiepomp vrijgave | Circulation pump release | Hot_Water_System | Warm water groep 2 | Hot water group 2 | Hot_Water_System | Circulatie pomp | Circulation pump | Pump | Schakelen | Switch | Status
228 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SHWP1-C | SHWP1-C | BO Mapper | (33) 001.TP-01S-- | 001 | tp | s | Transportpomp 1 vrijgave | Transport pump 1 release | Boiler | Ketel 1 | Boiler 1 | Boiler | Transportpomp | Transport pump | Pump | Schakelen | Switch | Status
229 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWP1-C | SCHWP1-C | BO Mapper | (33) 122.TP-01S-- | 122 | tp | s | Transportpomp 1 vrijgave | Transport pump 1 release | Chilled_Water_System | Gekoeld water groep 2 | Chilled water group 2 | Chilled_Water_System | Transportpomp | Transport pump | Pump | Schakelen | Switch | Status
230 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWP-C | SCHWP-C | BO Mapper | (33) 121.CP-01S-- | 121 | cp | s | Circulatiepomp vrijgave | Circulation pump release | Chilled_Water_System | Gekoeld water groep 1 | Chilled water group 1 | Chilled_Water_System | Circulatie pomp | Circulation pump | Pump | Schakelen | Switch | Status
231 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.TP-C | TP-C | BO Mapper | (33) 402.TP-01S-- | 402 | tp | s | Transportpomp bronnen vrijgave | Transfer pump resources release | Energy_Storage | Koudebron | Cold source | Energy_Storage | Transportpomp | Transport pump | Pump | Schakelen | Switch | Status
232 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CH1-C | CH1-C | BO Mapper | (33) 403.WP-01S-- | 403 | wp | s | Warmtepomp vrijgave | Heat pump release | Energy_Storage |  |  |  | Warmtepomp | Heat pump | Equipment | Schakelen | Switch | Status
233 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CWP1-C | CWP1-C | BO Mapper | (33) 403.CP-01S-- | 403 | cp | s | Circulatiepomp WP-CV vrijgave | Circulation pump WP-CV release | Energy_Storage |  |  |  | Circulatie pomp | Circulation pump | Pump | Schakelen | Switch | Status
234 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SM1-C | SM1-C | BO Mapper | (33) 402.CV-01S-- | 402 | cv | s | Wisselklep bronnen open sturen | Switching valve sources open | Energy_Storage | Koudebron | Cold source | Energy_Storage | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
235 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CWP1-C | CWP1-C | BO Mapper | (33) 404.CP-01S-- | 404 | cp | s | Circulatiepomp drogekoel. prim. vrijgave | Circulation pump dry cooling. prime. release | Energy_Storage |  |  |  | Circulatie pomp | Circulation pump | Pump | Schakelen | Switch | Status
236 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM1-C | SM1-C | BO Mapper | (33) 404.CV-01S-- | 404 | cv | s | Wisselklep drogekoeler open sturen | Open the dry cooler diverter valve | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
237 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CT1-C | CT1-C | BO Mapper | (33) 404.DK-01S-- | 404 | dk | s | Drogekoeler vrijgave | Dry cooler release | Energy_Storage |  |  |  | Doseer klep | Dosing valve | Valve | Schakelen | Switch | Status
238 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.301-AV1-C | 301-AV1-C | BO Mapper | (33) 301.VA-01S-- | 301 | va | s | Afzuigventilator horeca links vrijgave | Exhaust fan catering left release | Exhaust_Fan | Afzuig liftmachinekamer | Exhaust fan for machine room of elevator | Exhaust_Fan | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Schakelen | Switch | Status
239 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.302-AV1-C | 302-AV1-C | BO Mapper | (33) 302.VA-01S-- | 302 | va | s | Afzuigvent. containerruimte vrijgave | Exhaust vent. container room release | Exhaust_Fan | Afzuig toiletten | Exhaust fan for toilets | Exhaust_Fan | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Schakelen | Switch | Status
240 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.202-S-C | 202-S-C | BO Mapper | (33) 201.XS-01S-- | 201 | xs | s | LBK 202 in slave | AHU 202 in slave | AHU | LBK 1 | AHU 1 | AHU | Status algemeen | General status | Status | Schakelen | Switch | Status
241 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.EF-C | EF-C | BO Mapper | (33) 201.VA-01S-- | 201 | va | s | Afvoerventilator vrijgave | Exhaust fan release | AHU | LBK 1 | AHU 1 | AHU | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Schakelen | Switch | Status
242 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.HRW-C | HRW-C | BO Mapper | (33) 201.WW-01S-- | 201 | ww | s | Warmtewiel vrijgave | Heat wheel release | AHU | LBK 1 | AHU 1 | AHU | Warmtewiel | Rotary heat recovery | Heat_Wheel | Schakelen | Switch | Status
243 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.OAD-C | OAD-C | BO Mapper | (33) 201.CD-01S-- | 201 | cd | s | Aanzuigluchtklep vrijgave | Suction air valve release | AHU | LBK 1 | AHU 1 | AHU | Luchtklep | Air valve | Gas_Valve | Schakelen | Switch | Status
244 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.PHP-C | PHP-C | BO Mapper | (33) 201.CP-01S-- | 201 | cp | s | Circulatiepomp verw. vrijgave | circulation pump heating release | AHU | LBK 1 | AHU 1 | AHU | Circulatie pomp | Circulation pump | Pump | Schakelen | Switch | Status
245 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SF-C | SF-C | BO Mapper | (33) 201.VT-01S-- | 201 | vt | s | Toevoerventilator vrijgave | Supply fan release | AHU | LBK 1 | AHU 1 | AHU | Ventilator toevoer | Fan supply | Supply_Fan | Schakelen | Switch | Status
246 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.202-S-C | 202-S-C | BO Mapper | (33) 202.XS-01S-- | 202 | xs | s | LBK 202 in slave | AHU 202 in slave | AHU | LBK 2 | AHU 2 | AHU | Status algemeen | General status | Status | Schakelen | Switch | Status
247 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.EF-C | EF-C | BO Mapper | (33) 202.VA-01S-- | 202 | va | s | Afvoerventilator vrijgave | Exhaust fan release | AHU | LBK 2 | AHU 2 | AHU | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Schakelen | Switch | Status
248 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.HRW-C | HRW-C | BO Mapper | (33) 202.WW-01S-- | 202 | ww | s | Warmtewiel vrijgave | Heat wheel release | AHU | LBK 2 | AHU 2 | AHU | Warmtewiel | Rotary heat recovery | Heat_Wheel | Schakelen | Switch | Status
249 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.OAD-C | OAD-C | BO Mapper | (33) 202.CD-01S-- | 202 | cd | s | Aanzuigluchtklep vrijgave | Suction air valve release | AHU | LBK 2 | AHU 2 | AHU | Luchtklep | Air valve | Gas_Valve | Schakelen | Switch | Status
250 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.PHP-C | PHP-C | BO Mapper | (33) 202.CP-01S-- | 202 | cp | s | Circulatiepomp verw. vrijgave | circulation pump heating release | AHU | LBK 2 | AHU 2 | AHU | Circulatie pomp | Circulation pump | Pump | Schakelen | Switch | Status
251 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.SF-C | SF-C | BO Mapper | (33) 202.VT-01S-- | 202 | vt | s | Toevoerventilator vrijgave | Supply fan release | AHU | LBK 2 | AHU 2 | AHU | Ventilator toevoer | Fan supply | Supply_Fan | Schakelen | Switch | Status
252 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC014.ISO-FLR1-C | ISO-FLR1-C | BO Mapper | (33-0) 714.CV-01S-- | 714 | cv | s | Afsluiter vloerset 1 | Floor set valve 1 | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
253 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC030.ISOV-FLR-C | ISOV-FLR-C | BO Mapper | (33-2) 730.CV-01S-- | 730 | cv | s | Afsluiter open/dicht vloerset1 (zone C) | Shut-off valve open/close floor set1 (zone C) | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
254 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC021.ISO-FLR-C1 | ISO-FLR-C1 | BO Mapper | (33-1) 721.CV-01S-- | 721 | cv | s | Afsluiter vloerset 1 | Floor set valve 1 | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
255 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC026.ISO-FLR-C1 | ISO-FLR-C1 | BO Mapper | (33-2) 726.CV-01S-- | 726 | cv | s | Afsluiter vloerset 1 | Floor set valve 1 | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
256 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Spuiklep riool vrijgave open | Spuiklep riool vrijgave open | BO Mapper | (33) 413.CV-01S-- | 413 | cv | s | Spuiklep riool vrijgave open | Drain valve sewer release open | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
257 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Injectieklep KB vrijgave | Injectieklep KB vrijgave | BO Mapper | (33) 412.PC-01S-- | 412 | pc | s | Injectieklep koudebron vrijgave drukreg. | Injection valve cold source release pressure reg. | Energy_Storage |  |  |  | Drukregeling | Pressure control | Pressure_Setpoint | Schakelen | Switch | Status
258 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Warmebron pomp vrijgave | Warmebron pomp vrijgave | BO Mapper | (33) 413.BP-01S-- | 413 | bp | s | Warmebron pomp vrijgave | Heat source pump release | Energy_Storage |  |  |  | Bronpomp | Well pump | Water_Pump | Schakelen | Switch | Status
259 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Injectieklep WB vrijgave | Injectieklep WB vrijgave | BO Mapper | (33) 411.PC-01S-- | 411 | pc | s | Injectieklep warmebron vrijgave drukreg. | Injection valve hot source release pressure reg. | Energy_Storage |  |  |  | Drukregeling | Pressure control | Pressure_Setpoint | Schakelen | Switch | Status
260 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Klok reset drukhandhaving na 24h | Klok reset drukhandhaving na 24h | MSV Mapper | (33) 410.KL-01S-1 | 410 | kl | s | Klok reset drukhandhaving na 24h | Clock reset pressure hold after 24h | Energy_Storage |  |  |  | Klok | Clock | Reset_Command | Schakelen | Switch | Status
261 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CH1HP-C | CH1HP-C | BO Mapper | (33) 403.WP-01S1- | 403 | wp | s | Warmtepomp in heatpump bedrijf | Heat pump in heat pump operation | Energy_Storage |  |  |  | Warmtepomp | Heat pump | Equipment | Schakelen | Switch | Status
262 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Bronnen rust | O-Bronnen rust | MSV Mapper | (33) 410.XR-01S11 | 410 | xr | s | Bronnen rust | Sources rest | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Schakelen | Switch | Status
263 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Bronnen ontlaadbedrijf | O-Bronnen ontlaadbedrijf | MSV Mapper | (33) 410.XR-01S12 | 410 | xr | s | Bronnen ontlaadbedrijf | Resources unloading company | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Schakelen | Switch | Status
264 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Drukhandhaving bij vullen | O-Drukhandhaving bij vullen | MSV Mapper | (33) 410.XR-01S24 | 410 | xr | s | Drukhandhaving bij vullen | Pressure maintenance when filling | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Schakelen | Switch | Status
265 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Bronnen rust langer dan 5 min | O-Bronnen rust langer dan 5 min | MSV Mapper | (33) 410.XR-01S25 | 410 | xr | s | Bronnen rust langer dan 5 min | Sources rest longer than 5 min | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Schakelen | Switch | Status
266 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Einde spuien WB | O-Einde spuien WB | MSV Mapper | (33) 410.XR-01S26 | 410 | xr | s | Einde spuien WB | End of blowdown WB | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Schakelen | Switch | Status
267 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Einde spuien KB | O-Einde spuien KB | MSV Mapper | (33) 410.XR-01S27 | 410 | xr | s | Einde spuien KB | End of flushing KB | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Schakelen | Switch | Status
268 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Suppleren | O-Suppleren | MSV Mapper | (33) 410.XR-01S28 | 410 | xr | s | Suppleren | supplement | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Schakelen | Switch | Status
269 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Bronnen ontladen gevraagd | O-Bronnen ontladen gevraagd | MSV Mapper | (33) 410.XR-01S29 | 410 | xr | s | Bronnen ontladen gevraagd | Resources unload requested | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Schakelen | Switch | Status
270 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Bronnen laden gevraagd | O-Bronnen laden gevraagd | MSV Mapper | (33) 410.XR-01S30 | 410 | xr | s | Bronnen laden gevraagd | Requested to load resources | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Schakelen | Switch | Status
271 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Vraag spuien koude bron actief | O-Vraag spuien koude bron actief | MSV Mapper | (33) 410.XR-01S31 | 410 | xr | s | Vraag spuien koude bron actief | Demand blowdown cold source active | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Schakelen | Switch | Status
272 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Vraag spuien warme bron actief | O-Vraag spuien warme bron actief | MSV Mapper | (33) 410.XR-01S32 | 410 | xr | s | Vraag spuien warme bron actief | Demand blowdown hot source active | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Schakelen | Switch | Status
273 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Zet PSK Spuien op 0 | O-Zet PSK Spuien op 0 | MSV Mapper | (33) 410.XR-01S33 | 410 | xr | s | Zet PSK Spuien op 0 | Set PSK Flushing to 0 | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Schakelen | Switch | Status
274 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Bronnen laadbedrijf | O-Bronnen laadbedrijf | MSV Mapper | (33) 410.XR-01S5- | 410 | xr | s | Bronnen laadbedrijf | Resources loading company | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Schakelen | Switch | Status
275 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Bronnen paraat | O-Bronnen paraat | MSV Mapper | (33) 410.XR-01S7- | 410 | xr | s | Bronnen paraat | Sources ready | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Schakelen | Switch | Status
276 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Bronnen uit | O-Bronnen uit | MSV Mapper | (33) 410.XR-01S8- | 410 | xr | s | Bronnen uit | Sources out | Energy_Storage |  |  |  |  | Unknown – All data objects are defined for the thermal storage installation. |  | Schakelen | Switch | Status
277 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SYS-RESET | SYS-RESET | BI Mapper | (33) 801.RK-01SR- | 801 | rk | sr | Reset storing regelkast | Reset control box fault | Breaker_Panel | Schakelkast RK-01 | Electricity Control cabinet RK-01 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel | reset op afstand (GBS) | Remote reset (BMS) | Reset_Command
278 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.MISC-S | MISC-S | BI Mapper | (33) 801.RK-01SR- | 801 | rk | sr | Reset storing regelkast | Reset control box fault | Breaker_Panel | Schakelkast RK-01 | Electricity Control cabinet RK-01 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel | reset op afstand (GBS) | Remote reset (BMS) | Reset_Command
279 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Reset storing regelkast via GBS | Reset storing regelkast via GBS | BO Mapper | (33) 803.RK-01SR | 803 | rk | sr | Reset storing regelkast via GBS | Reset control box fault via BMS | Breaker_Panel |  |  |  | Regelkast | Control box, Switch box | Breaker_Panel | reset op afstand (GBS) | Remote reset (BMS) | Reset_Command
280 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Reset storing regelkast | Reset storing regelkast | BI Mapper | (33) 803.RK-01SR- | 803 | rk | sr | Reset storing regelkast | Reset control box fault | Breaker_Panel |  |  |  | Regelkast | Control box, Switch box | Breaker_Panel | reset op afstand (GBS) | Remote reset (BMS) | Reset_Command
281 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.RST-C | RST-C | BO Mapper | (33) 801.RK-01SR1 | 801 | rk | sr | Reset storing regelkast via GBS | Reset control box fault via BMS | Breaker_Panel | Schakelkast RK-01 | Electricity Control cabinet RK-01 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel | reset op afstand (GBS) | Remote reset (BMS) | Reset_Command
282 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.RESET-S | RESET-S | BI Mapper | (33) 802.RK-01SR1 | 802 | rk | sr | Reset storing | Reset fault | Breaker_Panel | Schakelkast RK-02 | Electricity Control cabinet RK-02 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel | reset op afstand (GBS) | Remote reset (BMS) | Reset_Command
283 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Reset storing IBS | Reset storing IBS | MSV Mapper | (33) 803.RK-01SR1 | 803 | rk | sr | Reset storing IBS (LCT) | Reset fault IBS (LCT) | Breaker_Panel |  |  |  | Regelkast | Control box, Switch box | Breaker_Panel | reset op afstand (GBS) | Remote reset (BMS) | Reset_Command
284 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SYS-RESET | SYS-RESET | BI Mapper | (33) 801.RK-01SR2 | 801 | rk | sr | Reset storing regelkast | Reset control box fault | Breaker_Panel | Schakelkast RK-01 | Electricity Control cabinet RK-01 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel | reset op afstand (GBS) | Remote reset (BMS) | Reset_Command
285 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.RESET-C | RESET-C | BO Mapper | (33) 802.RK-01SR2 | 802 | rk | sr | Reset storing regelkast | Reset control box fault | Breaker_Panel | Schakelkast RK-02 | Electricity Control cabinet RK-02 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel | reset op afstand (GBS) | Remote reset (BMS) | Reset_Command
286 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SU-C | SU-C | BO Mapper | (33) 801.RK-01SU- | 801 | rk | su | Verzamelstoring urgent | Collective fault urgent | Breaker_Panel | Schakelkast RK-01 | Electricity Control cabinet RK-01 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel | urgente storing | Urgent failure | Failure_Alarm
287 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SU-C | SU-C | BO Mapper | (33) 801.RK-01SU- | 801 | rk | su | Verzamelstoring urgent | Collective fault urgent | Breaker_Panel | Schakelkast RK-01 | Electricity Control cabinet RK-01 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel | brandschakelaar ventilatie uit | fire switch ventilation off command | Fire_Control_Panel
288 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SU-C | SU-C | BO Mapper | (33) 802.RK-01SU- | 802 | rk | su | Storing urgent | Malfunction urgent | Breaker_Panel | Schakelkast RK-02 | Electricity Control cabinet RK-02 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel | urgente storing | Urgent failure | Failure_Alarm
289 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SU-C | SU-C | BO Mapper | (33) 802.RK-01SU- | 802 | rk | su | Storing urgent | Malfunction urgent | Breaker_Panel | Schakelkast RK-02 | Electricity Control cabinet RK-02 | Breaker_Panel | Regelkast | Control box, Switch box | Breaker_Panel | brandschakelaar ventilatie uit | fire switch ventilation off command | Fire_Control_Panel
290 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Verzamelstoring | Verzamelstoring | BO Mapper | (33) 803.RK-01SU- | 803 | rk | su | Verzamelstoring | Collective failure | Breaker_Panel |  |  |  | Regelkast | Control box, Switch box | Breaker_Panel | urgente storing | Urgent failure | Failure_Alarm
291 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Verzamelstoring | Verzamelstoring | BO Mapper | (33) 803.RK-01SU- | 803 | rk | su | Verzamelstoring | Collective failure | Breaker_Panel |  |  |  | Regelkast | Control box, Switch box | Breaker_Panel | brandschakelaar ventilatie uit | fire switch ventilation off command | Fire_Control_Panel
292 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.HTG-O | HTG-O | AO Mapper | (33) 021.CV-01V-- | 021 | cv | v | Regelafsluiter CV | Control valve CV | Hot_Water_System | Warm water groep 1 | Hot water group 1 | Hot_Water_System | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
293 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.HTG-O | HTG-O | AO Mapper | (33) 022.CV-01V-- | 022 | cv | v | Regelafsluiter CV | Control valve CV | Hot_Water_System | Warm water groep 2 | Hot water group 2 | Hot_Water_System | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
294 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SHWP1-O | SHWP1-O | AO Mapper | (33) 001.TP-01V-- | 001 | tp | v | Transportpomp 1 sturing | Transport pump 1 control | Boiler | Ketel 1 | Boiler 1 | Boiler | Transportpomp | Transport pump | Pump | Sturing | Control (analog signal) | Command
295 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Voorreg GKW 121 SL-O | Voorreg GKW 121 SL-O | AO Mapper | (33) 121.CV-01V-- | 121 | cv | v | Regelafsluiter | Control valve | Chilled_Water_System | Gekoeld water groep 1 | Chilled water group 1 | Chilled_Water_System | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
296 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Voorreg GKW 122 SL-O | Voorreg GKW 122 SL-O | AO Mapper | (33) 122.CV-01V-- | 122 | cv | v | Regelafsluiter | Control valve | Chilled_Water_System | Gekoeld water groep 2 | Chilled water group 2 | Chilled_Water_System | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
297 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWP1-O | SCHWP1-O | AO Mapper | (33) 122.TP-01V-- | 122 | tp | v | Transportpomp 1 sturing | Transport pump 1 control | Chilled_Water_System | Gekoeld water groep 2 | Chilled water group 2 | Chilled_Water_System | Transportpomp | Transport pump | Pump | Sturing | Control (analog signal) | Command
298 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.TP W-K levering SL-O | TP W-K levering SL-O | AO Mapper | (33) 402.TP-01V-- | 402 | tp | v | Transportpomp bronnen sturing | Transport pump source control | Energy_Storage | Koudebron | Cold source | Energy_Storage | Transportpomp | Transport pump | Pump | Sturing | Control (analog signal) | Command
299 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Reg condensor SL-O | Reg condensor SL-O | AO Mapper | (33) 403.CV-01V-- | 403 | cv | v | Regelafsluiter WP-CV | Control valve WP-CV | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
300 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CWP1-O | CWP1-O | AO Mapper | (33) 404.CP-01V-- | 404 | cp | v | Circulatiepomp drogekoeler prim.sturing | Circulation pump dry cooler prime control | Energy_Storage |  |  |  | Circulatie pomp | Circulation pump | Pump | Sturing | Control (analog signal) | Command
301 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CT1-O | CT1-O | AO Mapper | (33) 404.DK-01V-- | 404 | dk | v | Drogekoeler sturing | Dry cooler control | Energy_Storage |  |  |  | Doseer klep | Dosing valve | Valve | Sturing | Control (analog signal) | Command
302 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.301-EF-O-1 | 301-EF-O-1 | AO Mapper | (33) 301.VA-01V-- | 301 | va | v | Afzuigventilator horeca links sturing | Exhaust fan catering left control | Exhaust_Fan | Afzuig liftmachinekamer | Exhaust fan for machine room of elevator | Exhaust_Fan | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Sturing | Control (analog signal) | Command
303 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SF-O | SF-O | AO Mapper | (33) 201.VT-01V-- | 201 | vt | v | Toevoerventilator sturing | Supply fan control | AHU | LBK 1 | AHU 1 | AHU | Ventilator toevoer | Fan supply | Supply_Fan | Sturing | Control (analog signal) | Command
304 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.EF-O | EF-O | AO Mapper | (33) 201.VA-01V-- | 201 | va | v | Afvoerventilator sturing | Exhaust fan control | AHU | LBK 1 | AHU 1 | AHU | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Sturing | Control (analog signal) | Command
305 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.HRW-O | HRW-O | AO Mapper | (33) 201.WW-01V-- | 201 | ww | v | Warmtewiel sturing | Heat wheel control | AHU | LBK 1 | AHU 1 | AHU | Warmtewiel | Rotary heat recovery | Heat_Wheel | Sturing | Control (analog signal) | Command
306 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.PH-O | PH-O | AO Mapper | (33) 201.CV-01V-- | 201 | cv | v | Regelafsluiter verwarmer | Control valve heater | AHU | LBK 1 | AHU 1 | AHU | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
307 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.SF-O | SF-O | AO Mapper | (33) 202.VT-01V-- | 202 | vt | v | Toevoerventilator sturing | Supply fan control | AHU | LBK 2 | AHU 2 | AHU | Ventilator toevoer | Fan supply | Supply_Fan | Sturing | Control (analog signal) | Command
308 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.EF-O | EF-O | AO Mapper | (33) 202.VA-01V-- | 202 | va | v | Afvoerventilator sturing | Exhaust fan control | AHU | LBK 2 | AHU 2 | AHU | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Sturing | Control (analog signal) | Command
309 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.HRW-O | HRW-O | AO Mapper | (33) 202.WW-01V-- | 202 | ww | v | Warmtewiel sturing | Heat wheel control | AHU | LBK 2 | AHU 2 | AHU | Warmtewiel | Rotary heat recovery | Heat_Wheel | Sturing | Control (analog signal) | Command
310 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.PH-O | PH-O | AO Mapper | (33) 202.CV-01V-- | 202 | cv | v | Regelafsluiter verwarmer | Control valve heater | AHU | LBK 2 | AHU 2 | AHU | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
311 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC011.HTG-O | HTG-O | AO Mapper | (33-0) 711.CV-01V-- | 711 | cv | v | Regelafsluiter CV | Control valve CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
312 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC012.HTG-O | HTG-O | AO Mapper | (33-0) 712.CV-01V-- | 712 | cv | v | Regelafsluiter CV | Control valve CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
313 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC013.HTG-O | HTG-O | AO Mapper | (33-0) 713.CV-01V-- | 713 | cv | v | Regelafsluiter CV | Control valve CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
314 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC016.HTG-O | HTG-O | AO Mapper | (33-0) 716.CV-01V-- | 716 | cv | v | Regelafsluiter CV | Control valve CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
315 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC017.HTG-O | HTG-O | AO Mapper | (33-0) 717.CV-01V-- | 717 | cv | v | Regelafsluiter CV | Control valve CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
316 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC018.HTG-O | HTG-O | AO Mapper | (33-0) 718.CV-01V-- | 718 | cv | v | Regelafsluiter CV | Control valve CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
317 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.HTG-O | HTG-O | AO Mapper | (33-1) 719.CV-01V-- | 719 | cv | v | Regelafsluiter CV | Control valve CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
318 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC020.HTG-O | HTG-O | AO Mapper | (33-1) 720.CV-01V-- | 720 | cv | v | Regelafsluiter CV | Control valve CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
319 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC022.HTG-O | HTG-O | AO Mapper | (33-1) 722.CV-01V-- | 722 | cv | v | Regelafsluiter CV | Control valve CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
320 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.HTG-O | HTG-O | AO Mapper | (33-1) 723.CV-01V-- | 723 | cv | v | Regelafsluiter CV | Control valve CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
321 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC024.HTG-O | HTG-O | AO Mapper | (33-2) 724.CV-01V-- | 724 | cv | v | Regelafsluiter CV | Control valve CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
322 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC025.HTG-O | HTG-O | AO Mapper | (33-2) 725.CV-01V-- | 725 | cv | v | Regelafsluiter CV | Control valve CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
323 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC027.HTG-O | HTG-O | AO Mapper | (33-2) 727.CV-01V-- | 727 | cv | v | Regelafsluiter CV | Control valve CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
324 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC028.HTG-O | HTG-O | AO Mapper | (33-2) 728.CV-01V-- | 728 | cv | v | Regelafsluiter CV | Control valve CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
325 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC029.HTG-O | HTG-O | AO Mapper | (33-2) 729.CV-01V-- | 729 | cv | v | Regelafsluiter CV | Control valve CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
326 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC031.HTG-O | HTG-O | AO Mapper | (33-2) 731.CV-01V-- | 731 | cv | v | Regelafsluiter CV | Control valve CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
327 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC011.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-0) 711.VAV01V-- | 711 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
328 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC013.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-0) 713.VAV01V-- | 713 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
329 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC016.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-0) 716.VAV01V-- | 716 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
330 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC017.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-0) 717.VAV01V-- | 717 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
331 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC018.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-0) 718.VAV01V-- | 718 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
332 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-1) 719.VAV01V-- | 719 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
333 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC020.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-1) 720.VAV01V-- | 720 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
334 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC021.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-1) 721.VAV01V-- | 721 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
335 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC022.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-1) 722.VAV01V-- | 722 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
336 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-1) 723.VAV01V-- | 723 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
337 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC024.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-2) 724.VAV01V-- | 724 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
338 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC025.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-2) 725.VAV01V-- | 725 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
339 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC026.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-2) 726.VAV01V-- | 726 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
340 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC027.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-2) 727.VAV01V-- | 727 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
341 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC028.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-2) 728.VAV01V-- | 728 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
342 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC029.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-2) 729.VAV01V-- | 729 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
343 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC031.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-2) 731.VAV01V-- | 731 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
344 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC030.DPR1-AV-O | DPR1-AV-O | AO Mapper | (33-2) 730.VAV01V-- | 730 | vav | v | Afvoerlucht VAV-1 sturing | Exhaust air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
345 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.202-SF-O | 202-SF-O | AO Mapper | (33) 201.VT-01V1- | 201 | vt | v | Sturing drukregeling naar LBK 202 | Control pressure regulation to LBK 202 | AHU | LBK 1 | AHU 1 | AHU | Ventilator toevoer | Fan supply | Supply_Fan | Sturing | Control (analog signal) | Command
346 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.202-EF-O | 202-EF-O | AO Mapper | (33) 201.VA-01V1- | 201 | va | v | Sturing drukregeling naar LBK 202 | Control pressure regulation to LBK 202 | AHU | LBK 1 | AHU 1 | AHU | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Sturing | Control (analog signal) | Command
347 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.CHW-SP | CHW-SP | AV Mapper | (33) 021.TC-01W-- (GKW) | 021 | tc | w | Werksetpoint Koeling | Working Setpoint Cooling | Hot_Water_System | Warm water groep 1 | Hot water group 1 | Hot_Water_System | Temperatuurregeling | Temperature regulation | Temperature | Werksetpunt | Operation set point | Setpoint
348 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.HW-SP | HW-SP | AV Mapper | (33) 021.TC-01W-- (CV) | 021 | tc | w | Werksetpoint Verwarming | Operating set point heating | Hot_Water_System | Warm water groep 1 | Hot water group 1 | Hot_Water_System | Temperatuurregeling | Temperature regulation | Temperature | Werksetpunt | Operation set point | Setpoint
349 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Parameters.HWZN-SP | HWZN-SP | AV Mapper | (33) 022.TC-01W-- (RT-CV) | 022 | tc | w | Werksetpoint Ruimte | Working setpoint Space | Hot_Water_System | Warm water groep 2 | Hot water group 2 | Hot_Water_System | Temperatuurregeling | Temperature regulation | Temperature | Werksetpunt | Operation set point | Setpoint
350 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Parameters.Setp CHW | Setp CHW | AV Mapper | (33) 022.TC-01W-- (R-GKW) | 022 | tc | w | Setpoint retourtemp. koeling | Setpoint return temp. cooling | Hot_Water_System | Warm water groep 2 | Hot water group 2 | Hot_Water_System | Temperatuurregeling | Temperature regulation | Temperature | Werksetpunt | Operation set point | Setpoint
351 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Parameters.Setp HW | Setp HW | AV Mapper | (33) 022.TC-01W-- (R-CV) | 022 | tc | w | Setpoint retoutemp. verwarming | Setpoint return temp. heating | Hot_Water_System | Warm water groep 2 | Hot water group 2 | Hot_Water_System | Temperatuurregeling | Temperature regulation | Temperature | Werksetpunt | Operation set point | Setpoint
352 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Parameters.TPW- K levering SLP-SP | TPW- K levering SLP-SP | AV Mapper | (33) 402.TP-01W-- | 402 | tp | w | Setpoint transportpomp | Transfer pump setpoint | Energy_Storage | Koudebron | Cold source | Energy_Storage | Transportpomp | Transport pump | Pump | Werksetpunt | Operation set point | Setpoint
353 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Network Inputs.I-DAP-SP | I-DAP-SP | AV Mapper | (33) 201.PC-01W-- | 201 | pc | w | Inblaasdruk Setpoint | Inlet Pressure Setpoint | AHU | LBK 1 | AHU 1 | AHU | Drukregeling | Pressure control | Pressure_Setpoint | Werksetpunt | Operation set point | Setpoint
354 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Network Outputs.O-EFFDAT-SP | O-EFFDAT-SP | AV Mapper | (33) 201.TC-01W-- | 201 | tc | w | Setpoint inblaastemp. | Set point inlet temp. | AHU | LBK 1 | AHU 1 | AHU | Temperatuurregeling | Temperature regulation | Temperature | Werksetpunt | Operation set point | Setpoint
355 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Network Inputs.I-DAP-SP | I-DAP-SP | AV Mapper | (33) 202.PC-01W-- | 202 | pc | w | Toevoerdruk Setpoint | Supply pressure Setpoint | AHU | LBK 2 | AHU 2 | AHU | Drukregeling | Pressure control | Pressure_Setpoint | Werksetpunt | Operation set point | Setpoint
356 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Network Outputs.O-EFFDAT-SP | O-EFFDAT-SP | AV Mapper | (33) 202.TC-01W-- | 202 | tc | w | Setpoint inblaastemp. | Set point inlet temp. | AHU | LBK 2 | AHU 2 | AHU | Temperatuurregeling | Temperature regulation | Temperature | Werksetpunt | Operation set point | Setpoint
357 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Max injectie temp WB ontladen | Max injectie temp WB ontladen | AV Mapper | (33) 411.TT-01W-- | 411 | tt | w | Max. injectie temp. WB ontladen | max. injection temp. WB discharged | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Werksetpunt | Operation set point | Setpoint
358 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Max injectie temp KB laden | Max injectie temp KB laden | AV Mapper | (33) 412.TT-01W-- | 412 | tt | w | Max. injectie temp. KB laden (9grd) | max. injection temp. Loading KB (9grd) | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Werksetpunt | Operation set point | Setpoint
359 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.EFFDAT-SP | EFFDAT-SP | AV Mapper | (33) 201.TC-01W1- | 201 | tc | w | Inblaas setpoint | Inlet setpoint | AHU | LBK 1 | AHU 1 | AHU | Temperatuurregeling | Temperature regulation | Temperature | Werksetpunt | Operation set point | Setpoint
360 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Parameters.EFFDAT-SP | EFFDAT-SP | AV Mapper | (33) 202.TC-01W1- | 202 | tc | w | Inblaas setpoint | Inlet setpoint | AHU | LBK 2 | AHU 2 | AHU | Temperatuurregeling | Temperature regulation | Temperature | Werksetpunt | Operation set point | Setpoint
361 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Werksetpoint flow bronnen | O-Werksetpoint flow bronnen | AV Mapper | (33) 410.FC-01W1- | 410 | fc | w | Werksetpoint flow bronnen | Working setpoint flow sources | Energy_Storage |  |  |  |  | Flow control | Flow_Sensor | Werksetpunt | Operation set point | Setpoint
362 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.DAT-OARSTA | DAT-OARSTA | AV Mapper | (33) 201.SL-01X1 | 201 | sl | x | StooklijnX1 | Heating curveX1 | AHU | LBK 1 | AHU 1 | AHU | Sloten | Locks | Lockout_Status | Instelling (X-as) | Configuration (X-axis) | Setpoint
363 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Parameters.DAT-OARSTA | DAT-OARSTA | AV Mapper | (33) 202.SL-01X1- | 202 | sl | x | Stooklijn X1 | Heating curve X1 | AHU | LBK 2 | AHU 2 | AHU | Sloten | Locks | Lockout_Status | Instelling (X-as) | Configuration (X-axis) | Setpoint
364 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.DAT-OARSTB | DAT-OARSTB | AV Mapper | (33) 201.SL-01X2- | 201 | sl | x | Stooklijn X2 | Heating curve X2 | AHU | LBK 1 | AHU 1 | AHU | Sloten | Locks | Lockout_Status | Instelling (X-as) | Configuration (X-axis) | Setpoint
365 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Parameters.DAT-OARSTB | DAT-OARSTB | AV Mapper | (33) 202.SL-01X2- | 202 | sl | x | Stooklijn X2 | Heating curve X2 | AHU | LBK 2 | AHU 2 | AHU | Sloten | Locks | Lockout_Status | Instelling (X-as) | Configuration (X-axis) | Setpoint
366 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.I-HWDP-SP | I-HWDP-SP | AV Mapper | (33) 001.PC-01XS- | 001 | pc | xs | Setpoint delta P | Set point delta P | Boiler | Ketel 1 | Boiler 1 | Boiler | Drukregeling | Pressure control | Pressure_Setpoint | Setpunt verstelling | Adjustment set point | Setpoint
367 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Network Inputs.I-SP-V | I-SP-V | AV Mapper | (33) 404.TC-01XS- | 404 | tc | xs | Verstelling setpoint droge koeler | Dry cooler set point adjustment | Energy_Storage |  |  |  | Temperatuurregeling | Temperature regulation | Temperature | Setpunt verstelling | Adjustment set point | Setpoint
368 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC014.ZN2-V | ZN2-V | AI Mapper | (33-0) 714.TC-01XS- | 714 | tc | xs | Ruimtetemperatuur verstell. | Room temperature adjust. | Equipment |  |  |  | Temperatuurregeling | Temperature regulation | Temperature | Setpunt verstelling | Adjustment set point | Setpoint
369 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Network Inputs.I-SP-V | I-SP-V | AV Mapper | (33) 20x.TC-01XS- | 20x | tc | xs | Setpoint verstelling inblaastemperatuur | Setpoint adjustment inlet temperature |  |  |  |  | Temperatuurregeling | Temperature regulation | Temperature | Setpunt verstelling | Adjustment set point | Setpoint
370 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Network Inputs.I-SP-V | I-SP-V | AV Mapper | (33) 202.TC-01XS- | 202 | tc | xs | Setpointverstelling inblaastemperatuur | Set point adjustment inlet temperature | AHU | LBK 2 | AHU 2 | AHU | Temperatuurregeling | Temperature regulation | Temperature | Setpunt verstelling | Adjustment set point | Setpoint
371 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Parameters.WSP GKW W-lev | WSP GKW W-lev | AV Mapper | (33) 403.TC-01XS1 | 403 | tc | xs | Setpoint GKW WP W-leveren | Setpoint GKW WP W-supply | Energy_Storage |  |  |  | Temperatuurregeling | Temperature regulation | Temperature | Setpunt verstelling | Adjustment set point | Setpoint
372 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Parameters.WSP GKW K-lev | WSP GKW K-lev | AV Mapper | (33) 403.TC-01XS2 | 403 | tc | xs | Setpoint GKW WP K-leveren | Setpoint GKW WP K-supply | Energy_Storage |  |  |  | Temperatuurregeling | Temperature regulation | Temperature | Setpunt verstelling | Adjustment set point | Setpoint
373 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.DATLO-SP | DATLO-SP | AV Mapper | (33) 201.SL-01Y1- | 201 | sl | y | Stooklijn Y1 | Heating curve Y1 | AHU | LBK 1 | AHU 1 | AHU | Sloten | Locks | Lockout_Status | Instelling (Y-as) | Configuration (Y-axis) | Setpoint
374 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Parameters.DATLO-SP | DATLO-SP | AV Mapper | (33) 202.SL-01Y1- | 202 | sl | y | Stooklijn Y1 | Heating curve Y1 | AHU | LBK 2 | AHU 2 | AHU | Sloten | Locks | Lockout_Status | Instelling (Y-as) | Configuration (Y-axis) | Setpoint
375 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.DATHI-SP | DATHI-SP | AV Mapper | (33) 201.SL-01Y2- | 201 | sl | y | Stooklijn Y2 | Heating curve Y2 | AHU | LBK 1 | AHU 1 | AHU | Sloten | Locks | Lockout_Status | Instelling (Y-as) | Configuration (Y-axis) | Setpoint
376 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Parameters.DATHI-SP | DATHI-SP | AV Mapper | (33) 202.SL-01Y2- | 202 | sl | y | Stooklijn Y2 | Heating curve Y2 | AHU | LBK 2 | AHU 2 | AHU | Sloten | Locks | Lockout_Status | Instelling (Y-as) | Configuration (Y-axis) | Setpoint
377 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SHWP2-FAULT | SHWP2-FAULT | BI Mapper | (33) 001.TP-02A-- | 001 | tp | a | Transportpomp 2 storing | Transport pump 2 malfunction | Boiler | Ketel 1 | Boiler 1 | Boiler | Transportpomp | Transport pump | Pump | Alarm | Alarm | Alarm
378 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.LA2-A | LA2-A | BI Mapper | (33) 901.LA-02A-- | 901 | la | a | Wateroverlast MER | Flooding EIA | Water_Loss_Alarm | Wateroverlast | Flooding water spill | Water_Loss_Alarm | Niveau alarm | Level alarm | Water_Level_Alarm | Alarm | Alarm | Alarm
379 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.MISC-A2 | MISC-A2 | BI Mapper | (33) 902.LV-02A-- | 902 | lv | a | Tracing vetvangleiding groep 2 storing | Tracing grease trap line group 2 failure | [5 empty] | Tracing grease trap line |  | Alarm | Alarm | Alarm
380 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.KNXU-A | KNXU-A | BI Mapper | (33) 918.XA-02A-- | 918 | xa | a | KNX installatie storing urgent | KNX installation fault urgent |  |  |  |  | Storing algemeen | Malfunction general | Fault_Status | Alarm | Alarm | Alarm
381 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Parameters.Vetvanger 2 tracing storing | Vetvanger 2 tracing storing | MSV Mapper | (33) 902.LV-02A-- | 902 | lv | a | Vetvanger 2 tracing storing | Grease trap 2 tracing failure | [5 empty] | Tracing grease trap line |  | Alarm | Alarm | Alarm
382 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWP2-FAULT | SCHWP2-FAULT | BI Mapper | (33) 122.TP-02A-- | 122 | tp | a | Transportpomp 2 storing | Transport pump 2 malfunction | Chilled_Water_System | Gekoeld water groep 2 | Chilled water group 2 | Chilled_Water_System | Transportpomp | Transport pump | Pump | Alarm | Alarm | Alarm
383 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.PCHWP1-FAULT | PCHWP1-FAULT | BI Mapper | (33) 403.CP-02A-- | 403 | cp | a | Circulatiepomp WP-GKW storing | Circulation pump WP-GKW malfunction | Energy_Storage |  |  |  | Circulatie pomp | Circulation pump | Pump | Alarm | Alarm | Alarm
384 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CWP2-FAULT | CWP2-FAULT | BI Mapper | (33) 404.CP-02A-- | 404 | cp | a | Circulatiepomp drogekoeler sec. storing | Circulation pump drycooler sec. malfunction | Energy_Storage |  |  |  | Circulatie pomp | Circulation pump | Pump | Alarm | Alarm | Alarm
385 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.301-AV2-A | 301-AV2-A | BI Mapper | (33) 301.VA-02A-- | 301 | va | a | Afzuigventilator horeca rechts storing | Exhaust fan catering right malfunction | Exhaust_Fan | Afzuig liftmachinekamer | Exhaust fan for machine room of elevator | Exhaust_Fan | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Alarm | Alarm | Alarm
386 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.EF-BA | EF-BA | MSV Mapper | (33) 201.PDA-02A-- | 201 | pda | a | Flow alarm afvoerventilator | Flow alarm exhaust fan | AHU | LBK 1 | AHU 1 | AHU | Drukverschil alarm | Pressure difference alarm | Pressure_Alarm | Alarm | Alarm | Alarm
387 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Parameters.EF-BA | EF-BA | MSV Mapper | (33) 202.PDA-02A-- | 202 | pda | a | Flow alarm afvoerventilator | Flow alarm exhaust fan | AHU | LBK 2 | AHU 2 | AHU | Drukverschil alarm | Pressure difference alarm | Pressure_Alarm | Alarm | Alarm | Alarm
388 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.OG2-A | OG2-A | BI Mapper | (33).041.OG-02A-- | 041 | og | a | Ontgasser 2 storing | Degasser 2 malfunction | Hot_Water_System |  |  |  |  | Degasser |  | Alarm | Alarm | Alarm
389 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Nivo storing WB | O-Nivo storing WB | MSV Mapper | (33) 410.LT-02A1- | 410 | lt | a | Nivo storing WB | Level malfunction WB | Energy_Storage |  |  |  | Nivo meting | Level measurement | Water_Level_Sensor | Alarm | Alarm | Alarm
390 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CH2-A1 | CH2-A1 | BI Mapper | (33).905.XA-02A1- | 905 | xa | a | Proceskoeling unit 2 storing urgent | Process cooling unit 2 malfunction urgent | Server_Room | SER/MER meldingen | MER = Main Equipment Room, SER = Satellite Equipment Room | Server_Room | Storing algemeen | Malfunction general | Fault_Status | Alarm | Alarm | Alarm
391 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Nivo onderhoudsmelding WB | O-Nivo onderhoudsmelding WB | MSV Mapper | (33) 410.LT-02A2- | 410 | lt | a | Nivo onderhoudsmelding WB | Level maintenance message WB | Energy_Storage |  |  |  | Nivo meting | Level measurement | Water_Level_Sensor | Alarm | Alarm | Alarm
392 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CH2-A2 | CH2-A2 | BI Mapper | (33).905.XA-02A2- | 905 | xa | a | Proceskoeling unit 2 storing niet urgent | Process cooling unit 2 malfunction not urgent | Server_Room | SER/MER meldingen | MER = Main Equipment Room, SER = Satellite Equipment Room | Server_Room | Storing algemeen | Malfunction general | Fault_Status | Alarm | Alarm | Alarm
393 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Outputs.O-Nivo storing WB spuien | O-Nivo storing WB spuien | MSV Mapper | (33) 410.LT-02A3- | 410 | lt | a | Nivo storing WB spuien | Level fault WB flush | Energy_Storage |  |  |  | Nivo meting | Level measurement | Water_Level_Sensor | Alarm | Alarm | Alarm
394 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SHWP2-S | SHWP2-S | BI Mapper | (33) 001.TP-02B-- | 001 | tp | b | Transportpomp 2 bedrijf | Transport pump 2 operation | Boiler | Ketel 1 | Boiler 1 | Boiler | Transportpomp | Transport pump | Pump | Bedrijfsmelding | Operation status | Status
395 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.MISC-S2 | MISC-S2 | BI Mapper | (33) 902.LV-02B-- | 902 | lv | b | Tracing vetvangleiding groep 2 bedrijf | Tracing grease trap line group 2 company | [5 empty] | Tracing grease trap line |  | Bedrijfsmelding | Operation status | Status
396 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWP2-S | SCHWP2-S | BI Mapper | (33) 122.TP-02B-- | 122 | tp | b | Transportpomp 2 bedrijf | Transport pump 2 operation | Chilled_Water_System | Gekoeld water groep 2 | Chilled water group 2 | Chilled_Water_System | Transportpomp | Transport pump | Pump | Bedrijfsmelding | Operation status | Status
397 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.PCHWP1-S | PCHWP1-S | BI Mapper | (33) 403.CP-02B-- | 403 | cp | b | Circulatiepomp WP-GKW bedrijf | Circulation pump WP-GKW operation | Energy_Storage |  |  |  | Circulatie pomp | Circulation pump | Pump | Bedrijfsmelding | Operation status | Status
398 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CWP2-S | CWP2-S | BI Mapper | (33) 404.CP-02B-- | 404 | cp | b | Circulatiepomp drogekoeler sec. bedrijf | Circulation pump drycooler sec. company | Energy_Storage |  |  |  | Circulatie pomp | Circulation pump | Pump | Bedrijfsmelding | Operation status | Status
399 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.301-HS-S-2 | 301-HS-S-2 | BI Mapper | (33) 301.HS-02B-- | 301 | hs | b | Handschakelaar uit/aan | Hand switch off/on | Exhaust_Fan | Afzuig liftmachinekamer | Exhaust fan for machine room of elevator | Exhaust_Fan |  | Switch (manual) | Switch | Bedrijfsmelding | Operation status | Status
400 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.301-AV2-B | 301-AV2-B | BI Mapper | (33) 301.VA-02B-- | 301 | va | b | Afzuigventilator horeca rechts bedrijf | Exhaust fan catering right company | Exhaust_Fan | Afzuig liftmachinekamer | Exhaust fan for machine room of elevator | Exhaust_Fan | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Bedrijfsmelding | Operation status | Status
401 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.OG-S | OG-S | BI Mapper | (33).041.OG-02B-- | 041 | og | b | Ontgasser bedriif | Degasser operation | Hot_Water_System |  |  |  |  | Degasser |  | Bedrijfsmelding | Operation status | Status
402 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.PHWE-T | PHWE-T | AI Mapper | (33) 001.TT-02M-- | 001 | tt | m | Retourtemperatuur CV | Return temperature central heating | Boiler | Ketel 1 | Boiler 1 | Boiler | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
403 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.MISCL-T | MISCL-T | AI Mapper | (33) 021.TT-02M-- | 021 | tt | m | Retourtemperatuur | Return temperature | Hot_Water_System | Warm water groep 1 | Hot water group 1 | Hot_Water_System | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
404 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.MISCL-T | MISCL-T | AI Mapper | (33) 022.TT-02M-- | 022 | tt | m | Retourtemperatuur | Return temperature | Hot_Water_System | Warm water groep 2 | Hot water group 2 | Hot_Water_System | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
405 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.PCHWE2-T | PCHWE2-T | AI Mapper | (33) 122.TT-02M-- | 122 | tt | m | Retourtemperatuur | Return temperature | Chilled_Water_System | Gekoeld water groep 2 | Chilled water group 2 | Chilled_Water_System | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
406 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.PCHWE1-T | PCHWE1-T | AI Mapper | (33) 121.TT-02M-- | 121 | tt | m | Retourtemperatuur | Return temperature | Chilled_Water_System | Gekoeld water groep 1 | Chilled water group 1 | Chilled_Water_System | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
407 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWE2-T | SCHWE2-T | AI Mapper | (33) 402.TT-02M-- | 402 | tt | m | Retourtemperatuur 1 bronnen | Return temperature 1 sources | Energy_Storage | Koudebron | Cold source | Energy_Storage | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
408 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CH1CWR-T | CH1CWR-T | AI Mapper | (33) 403.TT-02M-- | 403 | tt | m | Retourtemperatuur WP-CV | Return temperature HP-CV | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
409 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CWR1-T | CWR1-T | AI Mapper | (33) 404.TT-02M-- | 404 | tt | m | Retourtemperatuur prim. | Return temperature prim. | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
410 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.203-EA-T | 203-EA-T | AI Mapper | (33) 203.TT-02M-- | 203 | tt | m | Retourluchttemperatuur LBK1 en LBK2 | Return air temperature AHU1 and AHU2 | AHU |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
411 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.301-EF-RPM-2 | 301-EF-RPM-2 | AI Mapper | (33) 301.VA-02M-- | 301 | va | m | Afzuigventilator horeca recht terugkop. | Exhaust fan catering straight back. | Exhaust_Fan | Afzuig liftmachinekamer | Exhaust fan for machine room of elevator | Exhaust_Fan | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Meting | Measurement | Sensor
412 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.203-EA-Q | 203-EA-Q | AI Mapper | (33) 203.QT-02M-- | 203 | qt | m | Retourluchtkwaliteit LBK1 en LBK2 | Return air quality AHU1 and AHU2 | AHU |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
413 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.203-EA-H | 203-EA-H | AI Mapper | (33) 203.MT-02M-- | 203 | mt | m | Retourluchtvochtigheid LBK1 en LBK2 | Return air humidity AHU1 and AHU2 | AHU |  |  |  | Vocht transmitter | Moisture transmitter | Humidity_Sensor | Meting | Measurement | Sensor
414 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.EA-P | EA-P | AI Mapper | (33) 201.PT-02M-- | 201 | pt | m | Afvoerdruk | Discharge pressure | AHU | LBK 1 | AHU 1 | AHU |  | Pressure transmitter | Pressure_Sensor | Meting | Measurement | Sensor
415 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.EA-P | EA-P | AI Mapper | (33) 202.PT-02M-- | 202 | pt | m | Afvoerdruk | Discharge pressure | AHU | LBK 2 | AHU 2 | AHU |  | Pressure transmitter | Pressure_Sensor | Meting | Measurement | Sensor
416 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC011.RHWL-T | RHWL-T | AI Mapper | (33-0) 711.TT-02M-- | 711 | tt | m | Retourwateropnemer | Return water sensor | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
417 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC012.RHWL-T | RHWL-T | AI Mapper | (33-0) 712.TT-02M-- | 712 | tt | m | Retourwateropnemer | Return water sensor | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
418 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC013.RHWL-T | RHWL-T | AI Mapper | (33-0) 713.TT-02M-- | 713 | tt | m | Retourwateropnemer | Return water sensor | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
419 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.RHWL-T | RHWL-T | AI Mapper | (33-1) 719.TT-02M-- | 719 | tt | m | Retourwateropnemer | Return water sensor | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
420 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC020.RHWL-T | RHWL-T | AI Mapper | (33-1) 720.TT-02M-- | 720 | tt | m | Retourwateropnemer | Return water sensor | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
421 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC022.RHWL-T | RHWL-T | AI Mapper | (33-1) 722.TT-02M-- | 722 | tt | m | Retourwateropnemer | Return water sensor | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
422 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.RHWL-T | RHWL-T | AI Mapper | (33-1) 723.TT-02M-- | 723 | tt | m | Retourwateropnemer | Return water sensor | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
423 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC024.RHWL-T | RHWL-T | AI Mapper | (33-2) 724.TT-02M-- | 724 | tt | m | Retourwateropnemer | Return water sensor | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
424 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC025.RHWL-T | RHWL-T | AI Mapper | (33-2) 725.TT-02M-- | 725 | tt | m | Retourwateropnemer | Return water sensor | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
425 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC027.RHWL-T | RHWL-T | AI Mapper | (33-2) 727.TT-02M-- | 727 | tt | m | Retourwateropnemer | Return water sensor | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
426 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC028.RHWL-T | RHWL-T | AI Mapper | (33-2) 728.TT-02M-- | 728 | tt | m | Retourwateropnemer | Return water sensor | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
427 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC029.RHWL-T | RHWL-T | AI Mapper | (33-2) 729.TT-02M-- | 729 | tt | m | Retourwateropnemer | Return water sensor | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
428 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC031.RHWL-T | RHWL-T | AI Mapper | (33-2) 731.TT-02M-- | 731 | tt | m | Retourwateropnemer | Return water sensor | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
429 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC012.Network Outputs.O-TV2-O | O-TV2-O | AV Mapper | (33-0) 711.QT-02M-- | 711 | qt | m | Luchthoeveelheid | Air quantity | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
430 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC013.Network Outputs.O-TV2-O | O-TV2-O | AV Mapper | (33-0) 713.QT-02M-- | 713 | qt | m | Flow berekening TV2 | Flow calculation TV2 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
431 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC015.Network Outputs.O-AV2-O | O-AV2-O | AV Mapper | (33-0) 715.QT-02M-- | 715 | qt | m | luchthoeveelheid | air volume | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
432 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.Network Outputs.O-TV2-O | O-TV2-O | AV Mapper | (33-1) 719.QT-02M-- | 719 | qt | m | Luchthoeveelheid | Air quantity | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
433 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC020.Network Outputs.O-TV2-O | O-TV2-O | AV Mapper | (33-1) 720.QT-02M-- | 720 | qt | m | luchthoeveelheid | air volume | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
434 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.Network Outputs.O-TV2-O | O-TV2-O | AV Mapper | (33-1) 723.QT-02M-- | 723 | qt | m | Flow berekening TV2 | Flow calculation TV2 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
435 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC026.Network Outputs.O-AV1-O | O-AV1-O | AV Mapper | (33-2) 726.QT-02M-- | 726 | qt | m | Flow berekening V1 | Flow calculation V1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
436 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC027.Network Outputs.O-AV1-O | O-AV1-O | AV Mapper | (33-2) 727.QT-02M-- | 727 | qt | m | Flow berekening V1 | Flow calculation V1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
437 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC028.Network Outputs.O-AV1-O | O-AV1-O | AV Mapper | (33-2) 728.QT-02M-- | 728 | qt | m | Flow berekening V1 | Flow calculation V1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
438 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC024.Network Outputs.O-AV1-O | O-AV1-O | AV Mapper | (33-2) 724.QT-02M-- | 724 | qt | m | Flow berekening AV1 | Flow calculation AV1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
439 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC031.Network Outputs.O-AV1-O | O-AV1-O | AV Mapper | (33-2) 731.QT-02M-- | 731 | qt | m | Flow berekening AV1 | Flow calculation AV1 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
440 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.EAFILT-DP | EAFILT-DP | AI Mapper | (33) 201.PDT02M-- | 201 | pdt | m | Drukverschil afvoerfilter | Pressure differential drain filter | AHU | LBK 1 | AHU 1 | AHU | Drukverschil meting | Differential pressure measurement | Differential_Pressure_Sensor | Meting | Measurement | Sensor
441 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.EAFILT-DP | EAFILT-DP | AI Mapper | (33) 202.PDT02M-- | 202 | pdt | m | Drukverschil afvoerfilter | Pressure differential drain filter | AHU | LBK 2 | AHU 2 | AHU | Drukverschil meting | Differential pressure measurement | Differential_Pressure_Sensor | Meting | Measurement | Sensor
442 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SM2-OP | SM2-OP | BI Mapper | (33) 402.CV-02O-- | 402 | cv | o | Wisselklep bronnen open | Diverter valve sources open | Energy_Storage | Koudebron | Cold source | Energy_Storage | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
443 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM2-OP | SM2-OP | BI Mapper | (33) 404.CV-02O-- | 404 | cv | o | Wisselklep drogekoeler open | Drycooler diverter valve open | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
444 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.BK-02-O | BK-02-O | BI Mapper | (33) 203.BK-02O-- | 203 | bk | o | Brandkleppen open cluster 1-1 | Fire dampers open cluster 1-1 | AHU |  |  |  |  | Firedamper | Damper | Open | Open | Open_Close_Status
445 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.EAD-O | EAD-O | BI Mapper | (33) 201.CD-02O-- | 201 | cd | o | Afblaasluchtklep open | Exhaust air valve open | AHU | LBK 1 | AHU 1 | AHU | Luchtklep | Air valve | Gas_Valve | Open | Open | Open_Close_Status
446 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.EAD-O | EAD-O | BI Mapper | (33) 202.CD-02O-- | 202 | cd | o | Afblaasluchtklep open | Exhaust air valve open | AHU | LBK 2 | AHU 2 | AHU | Luchtklep | Air valve | Gas_Valve | Open | Open | Open_Close_Status
447 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.MISC-C2 | MISC-C2 | BO Mapper | (33) 902.LV-02S-- | 902 | lv | s | Tracing vetvangleiding groep 2 vrijgave | Tracing grease trap group 2 release | [5 empty] | Tracing grease trap line |  | Schakelen | Switch | Status
448 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SHWP2-C | SHWP2-C | BO Mapper | (33) 001.TP-02S-- | 001 | tp | s | Transportpomp 2 vrijgave | Transport pump 2 release | Boiler | Ketel 1 | Boiler 1 | Boiler | Transportpomp | Transport pump | Pump | Schakelen | Switch | Status
449 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWP2-C | SCHWP2-C | BO Mapper | (33) 122.TP-02S-- | 122 | tp | s | Transportpomp 2 vrijgave | Transport pump 2 release | Chilled_Water_System | Gekoeld water groep 2 | Chilled water group 2 | Chilled_Water_System | Transportpomp | Transport pump | Pump | Schakelen | Switch | Status
450 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SM2-C | SM2-C | BO Mapper | (33) 402.CV-02S-- | 402 | cv | s | Wisselklep bronnen open sturen | Switching valve sources open | Energy_Storage | Koudebron | Cold source | Energy_Storage | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
451 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.PCHWP1-C | PCHWP1-C | BO Mapper | (33) 403.CP-02S-- | 403 | cp | s | Circulatiepomp WP-GKW vrijgave | Circulation pump WP-GKW release | Energy_Storage |  |  |  | Circulatie pomp | Circulation pump | Pump | Schakelen | Switch | Status
452 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CWP2-C | CWP2-C | BO Mapper | (33) 404.CP-02S-- | 404 | cp | s | Circulatiepomp drogekoeler sec. vrijgave | Circulation pump drycooler sec. release | Energy_Storage |  |  |  | Circulatie pomp | Circulation pump | Pump | Schakelen | Switch | Status
453 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM2-C | SM2-C | BO Mapper | (33) 404.CV-02S-- | 404 | cv | s | Wisselklep drogekoeler open sturen | Open the dry cooler diverter valve | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
454 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.301-AV2-C | 301-AV2-C | BO Mapper | (33) 301.VA-02S-- | 301 | va | s | Afzuigventilator horeca rechts vrijgave | Exhaust fan catering right release | Exhaust_Fan | Afzuig liftmachinekamer | Exhaust fan for machine room of elevator | Exhaust_Fan | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Schakelen | Switch | Status
455 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.EAD-C | EAD-C | BO Mapper | (33) 201.CD-02S-- | 201 | cd | s | Afblaasluchtklep vrijgave | Exhaust air valve release | AHU | LBK 1 | AHU 1 | AHU | Luchtklep | Air valve | Gas_Valve | Schakelen | Switch | Status
456 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.EAD-C | EAD-C | BO Mapper | (33) 202.CD-02S-- | 202 | cd | s | Afblaasluchtklep vrijgave | Exhaust air valve release | AHU | LBK 2 | AHU 2 | AHU | Luchtklep | Air valve | Gas_Valve | Schakelen | Switch | Status
457 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC021.ISO-FLR-C2 | ISO-FLR-C2 | BO Mapper | (33-1) 721.CV-02S-- | 721 | cv | s | Afsluiter vloerset 2 | Valve floor set 2 | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
458 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC026.ISO-FLR-C2 | ISO-FLR-C2 | BO Mapper | (33-2) 726.CV-02S-- | 726 | cv | s | Afsluiter vloerset 2 | Valve floor set 2 | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
459 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Koudebron pompen vrijgave | Koudebron pompen vrijgave | BO Mapper | (33) 413.BP-02S-- | 413 | bp | s | Koudebron pomp vrijgave | Cold source pump release | Energy_Storage |  |  |  | Bronpomp | Well pump | Water_Pump | Schakelen | Switch | Status
460 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.OG2-S | OG2-S | BI Mapper | (33).041.OG-02S-- | 041 | og | s | Ontgasser 2 bedrijf | Degasser 2 operation | Hot_Water_System |  |  |  |  | Degasser |  | Schakelen | Switch | Status
461 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CLG-O | CLG-O | AO Mapper | (33) 021.CV-02V-- | 021 | cv | v | Regelafsluiter GKW | Control valve GKW | Hot_Water_System | Warm water groep 1 | Hot water group 1 | Hot_Water_System | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
462 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.CLG-O | CLG-O | AO Mapper | (33) 022.CV-02V-- | 022 | cv | v | Regelafsluiter GKW | Control valve GKW | Hot_Water_System | Warm water groep 2 | Hot water group 2 | Hot_Water_System | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
463 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SHWP2-O | SHWP2-O | AO Mapper | (33) 001.TP-02V-- | 001 | tp | v | Transportpomp 2 sturing | Transport pump 2 control | Boiler | Ketel 1 | Boiler 1 | Boiler | Transportpomp | Transport pump | Pump | Sturing | Control (analog signal) | Command
464 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWP2-O | SCHWP2-O | AO Mapper | (33) 122.TP-02V-- | 122 | tp | v | Transportpomp 2 sturing | Transport pump 2 control | Chilled_Water_System | Gekoeld water groep 2 | Chilled water group 2 | Chilled_Water_System | Transportpomp | Transport pump | Pump | Sturing | Control (analog signal) | Command
465 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Reg verdamper SL-O | Reg verdamper SL-O | AO Mapper | (33) 403.CV-02V-- | 403 | cv | v | Regelafsluiter WP-GKW | Control valve WP-GKW | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
466 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CWP2-O | CWP2-O | AO Mapper | (33) 404.CP-02V-- | 404 | cp | v | Circulatiepomp drogekoeler sec.sturing | Circulation pump dry cooler sec.control | Energy_Storage |  |  |  | Circulatie pomp | Circulation pump | Pump | Sturing | Control (analog signal) | Command
467 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CLG-O | CLG-O | AO Mapper | (33) 201.CV-02V-- | 201 | cv | v | Regelafsluiter koeler | Cooler control valve | AHU | LBK 1 | AHU 1 | AHU | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
468 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.CLG-O | CLG-O | AO Mapper | (33) 202.CV-02V-- | 202 | cv | v | Regelafsluiter koeler | Cooler control valve | AHU | LBK 2 | AHU 2 | AHU | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
469 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.301-EF-O-2 | 301-EF-O-2 | AO Mapper | (33) 301.VA-02V-- | 301 | va | v | Afzuigventilator horeca recht sturing | Exhaust fan catering straight control | Exhaust_Fan | Afzuig liftmachinekamer | Exhaust fan for machine room of elevator | Exhaust_Fan | Afzuig ventilator | Exhaust fan | Exhaust_Fan | Sturing | Control (analog signal) | Command
470 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC011.CLG-O | CLG-O | AO Mapper | (33-0) 711.CV-02V-- | 711 | cv | v | Regelafsluiter GKW | Control valve GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
471 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC012.CLG-O | CLG-O | AO Mapper | (33-0) 712.CV-02V-- | 712 | cv | v | Regelafsluiter GKW | Control valve GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
472 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC013.CLG-O | CLG-O | AO Mapper | (33-0) 713.CV-02V-- | 713 | cv | v | Regelafsluiter GKW | Control valve GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
473 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.CLG-O | CLG-O | AO Mapper | (33-1) 719.CV-02V-- | 719 | cv | v | Regelafsluiter GKW | Control valve GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
474 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC020.CLG-O | CLG-O | AO Mapper | (33-1) 720.CV-02V-- | 720 | cv | v | Regelafsluiter GKW | Control valve GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
475 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC022.CLG-O | CLG-O | AO Mapper | (33-1) 722.CV-02V-- | 722 | cv | v | Regelafsluiter GKW | Control valve GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
476 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.CLG-O | CLG-O | AO Mapper | (33-1) 723.CV-02V-- | 723 | cv | v | Regelafsluiter GKW | Control valve GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
477 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC024.CLG-O | CLG-O | AO Mapper | (33-2) 724.CV-02V-- | 724 | cv | v | Regelafsluiter GKW | Control valve GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
478 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC025.CLG-O | CLG-O | AO Mapper | (33-2) 725.CV-02V-- | 725 | cv | v | Regelafsluiter GKW | Control valve GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
479 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC027.CLG-O | CLG-O | AO Mapper | (33-2) 727.CV-02V-- | 727 | cv | v | Regelafsluiter GKW | Control valve GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
480 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC028.CLG-O | CLG-O | AO Mapper | (33-2) 728.CV-02V-- | 728 | cv | v | Regelafsluiter GKW | Control valve GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
481 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC029.CLG-O | CLG-O | AO Mapper | (33-2) 728.CV-02V-- | 728 | cv | v | Regelafsluiter GKW | Control valve GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
482 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC031.CLG-O | CLG-O | AO Mapper | (33-2) 731.CV-02V-- | 731 | cv | v | Regelafsluiter GKW | Control valve GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
483 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC013.DPR2-TV-O | DPR2-TV-O | AO Mapper | (33-0) 713.VAV02V-- | 713 | vav | v | Toevoerlucht VAV-2 sturing | Supply air VAV-2 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
484 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC015.DPR2-AV-O | DPR2-AV-O | AO Mapper | (33-0) 715.VAV02V-- | 715 | vav | v | Afvoerlucht VAV-2 sturing | Exhaust air VAV-2 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
485 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.DPR2-TV-O | DPR2-TV-O | AO Mapper | (33-1) 719.VAV02V-- | 719 | vav | v | Toevoerlucht VAV-2 sturing | Supply air VAV-2 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
486 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC020.DPR2-TV-O | DPR2-TV-O | AO Mapper | (33-1) 720.VAV02V-- | 720 | vav | v | Toevoerlucht VAV-2 sturing | Supply air VAV-2 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
487 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC022.DPR2-TV-O | DPR2-TV-O | AO Mapper | (33-1) 722.VAV02V-- | 722 | vav | v | Toevoerlucht VAV-2 sturing | Supply air VAV-2 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
488 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.DPR2-TV-O | DPR2-TV-O | AO Mapper | (33-1) 723.VAV02V-- | 723 | vav | v | Toevoerlucht VAV-2 sturing | Supply air VAV-2 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
489 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC024.DPR3-AV-O | DPR3-AV-O | AO Mapper | (33-2) 724.VAV02V-- | 724 | vav | v | Afvoerlucht VAV-1 sturing | Exhaust air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
490 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC026.DPR3-AV-O | DPR3-AV-O | AO Mapper | (33-2) 726.VAV02V-- | 726 | vav | v | Afvoerlucht VAV-1 sturing | Exhaust air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
491 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC031.DPR3-AV-O | DPR3-AV-O | AO Mapper | (33-2) 731.VAV02V-- | 731 | vav | v | Afvoerlucht VAV-1 sturing | Exhaust air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
492 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC027.DPR1-AV-O | DPR1-AV-O | AO Mapper | (33-2) 727.VAV02V-- | 727 | vav | v | Afvoerlucht VAV-1 sturing | Exhaust air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
493 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC028.DPR1-AV-O | DPR1-AV-O | AO Mapper | (33-2) 728.VAV02V-- | 728 | vav | v | Afvoerlucht VAV-1 sturing | Exhaust air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
494 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Network Inputs.I-BLDGP-SP | I-BLDGP-SP | AV Mapper | (33) 201.PC-02W-- | 201 | pc | w | Afvoerdruk Setpoint | Discharge Pressure Setpoint | AHU | LBK 1 | AHU 1 | AHU | Drukregeling | Pressure control | Pressure_Setpoint | Werksetpunt | Operation set point | Setpoint
495 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Network Inputs.I-BLDGP-SP | I-BLDGP-SP | AV Mapper | (33) 202.PC-02W-- | 202 | pc | w | Afzuigdruk Setpoint | Suction Pressure Setpoint | AHU | LBK 2 | AHU 2 | AHU | Drukregeling | Pressure control | Pressure_Setpoint | Werksetpunt | Operation set point | Setpoint
496 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Parameters.WSP CV WP W-lev | WSP CV WP W-lev | AV Mapper | (33) 403.TC-02XS1 | 403 | tc | xs | Setpoint CV WP W-leveren | Setpoint CV HP W-supply | Energy_Storage |  |  |  | Temperatuurregeling | Temperature regulation | Temperature | Setpunt verstelling | Adjustment set point | Setpoint
497 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Parameters.WSP CV WP K-lev | WSP CV WP K-lev | AV Mapper | (33) 403.TC-02XS2 | 403 | tc | xs | Setpoint CV WP K-leveren | Setpoint CV HP K-supply | Energy_Storage |  |  |  | Temperatuurregeling | Temperature regulation | Temperature | Setpunt verstelling | Adjustment set point | Setpoint
498 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.LA3-A | LA3-A | BI Mapper | (33) 901.LA-03A-- | 901 | la | a | Wateroverlast DC ruimte | Flooding DC space | Water_Loss_Alarm | Wateroverlast | Flooding water spill | Water_Loss_Alarm | Niveau alarm | Level alarm | Water_Level_Alarm | Alarm | Alarm | Alarm
499 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.P FILT-A | P FILT-A | MSV Mapper | (33) 201.PDA-03A-- | 201 | pda | a | Toevoerfilter vervuild | Supply filter dirty | AHU | LBK 1 | AHU 1 | AHU | Drukverschil alarm | Pressure difference alarm | Pressure_Alarm | Alarm | Alarm | Alarm
500 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Parameters.P FILT-A | P FILT-A | MSV Mapper | (33) 202.PDA-03A-- | 202 | pda | a | Toevoerfilter vervuild | Supply filter dirty | AHU | LBK 2 | AHU 2 | AHU | Drukverschil alarm | Pressure difference alarm | Pressure_Alarm | Alarm | Alarm | Alarm
501 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.HTG-CL-ALM | HTG-CL-ALM | MSV Mapper | (33) 201.CV-03A1- | 201 | cv | a | Afsluiter CV niet dicht | Central heating shut-off valve not closed | AHU | LBK 1 | AHU 1 | AHU | Regelafsluiter | Regulating valve | Valve | Alarm | Alarm | Alarm
502 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Parameters.HTG-CL-ALM | HTG-CL-ALM | MSV Mapper | (33) 202.CV-03A1- | 202 | cv | a | Afsluiter CV niet dicht | Central heating shut-off valve not closed | AHU | LBK 2 | AHU 2 | AHU | Regelafsluiter | Regulating valve | Valve | Alarm | Alarm | Alarm
503 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.HTG-O-ALM | HTG-O-ALM | MSV Mapper | (33) 201.CV-03A2- | 201 | cv | a | Afsluiter CV niet open | Central heating shut-off valve not open | AHU | LBK 1 | AHU 1 | AHU | Regelafsluiter | Regulating valve | Valve | Alarm | Alarm | Alarm
504 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Parameters.HTG-O-ALM | HTG-O-ALM | MSV Mapper | (33) 202.CV-03A2- | 202 | cv | a | Afsluiter CV niet open | Central heating shut-off valve not open | AHU | LBK 2 | AHU 2 | AHU | Regelafsluiter | Regulating valve | Valve | Alarm | Alarm | Alarm
505 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWE3-T | SCHWE3-T | AI Mapper | (33) 402.TT-03M-- | 402 | tt | m | Retourtemperatuur 2 bronnen | Return temperature 2 wells | Energy_Storage | Koudebron | Cold source | Energy_Storage | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
506 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CH1CHWS-T | CH1CHWS-T | AI Mapper | (33) 403.TT-03M-- | 403 | tt | m | Aanvoertemperatuur WP-GKW | Flow temperature HP-GKW | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
507 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CWS1-T | CWS1-T | AI Mapper | (33) 404.TT-03M-- | 404 | tt | m | Aanvoertemperatuur sec. | Flow temperature sec. | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
508 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.OA-T | OA-T | AI Mapper | (33) 201.TT-03M-- | 201 | tt | m | Aanzuigluchttemperatuur | Suction air temperature | AHU | LBK 1 | AHU 1 | AHU | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
509 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.OA-T | OA-T | AI Mapper | (33) 202.TT-03M-- | 202 | tt | m | Aanzuigluchttemperatuur | Suction air temperature | AHU | LBK 2 | AHU 2 | AHU | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
510 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC015.Network Outputs.O-AV3-O | O-AV3-O | AV Mapper | (33-0) 715.QT-03M-- | 715 | qt | m | Luchthoeveelheid | Air quantity | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
511 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.Network Outputs.O-AV1-O | O-AV1-O | AV Mapper | (33-1) 719.QT-03M-- | 719 | qt | m | Luchthoeveelheid | Air quantity | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
512 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC022.Network Outputs.O-AV1-O | O-AV1-O | AV Mapper | (33-1) 722.QT-03M-- | 722 | qt | m | Flow berekening V3 | Flow calculation V3 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
513 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.Network Outputs.O-AV1-O | O-AV1-O | AV Mapper | (33-1) 723.QT-03M-- | 723 | qt | m | Flow berekening V3 | Flow calculation V3 | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
514 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.HTGVALVE-OP | HTGVALVE-OP | BI Mapper | (33) 021.CV-03O-- | 021 | cv | o | Vlinderklep CV open | Butterfly valve CV open | Hot_Water_System | Warm water groep 1 | Hot water group 1 | Hot_Water_System | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
515 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.HTGVALVE-OP | HTGVALVE-OP | BI Mapper | (33) 022.CV-03O-- | 022 | cv | o | Vlinderklep CV open | Butterfly valve CV open | Hot_Water_System | Warm water groep 2 | Hot water group 2 | Hot_Water_System | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
516 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SM3-OP | SM3-OP | BI Mapper | (33) 402.CV-03O-- | 402 | cv | o | Wisselklep bronnen open | Diverter valve sources open | Energy_Storage | Koudebron | Cold source | Energy_Storage | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
517 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM3-OP | SM3-OP | BI Mapper | (33) 404.CV-03O-- | 404 | cv | o | Wisselklep drogekoeler open | Drycooler diverter valve open | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
518 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.BK-03-O | BK-03-O | BI Mapper | (33) 203.BK-03O-- | 203 | bk | o | Brandkleppen open cluster 1-2 | Fire dampers open cluster 1-2 | AHU |  |  |  |  | Firedamper | Damper | Open | Open | Open_Close_Status
519 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.HTGV-OP | HTGV-OP | BI Mapper | (33) 201.CV-03O-- | 201 | cv | o | Vlinderklep CV open | Butterfly valve CV open | AHU | LBK 1 | AHU 1 | AHU | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
520 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.HTGV-OP | HTGV-OP | BI Mapper | (33) 202.CV-03O-- | 202 | cv | o | Vlinderklep CV open | Butterfly valve CV open | AHU | LBK 2 | AHU 2 | AHU | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
521 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.HTGVALVE-C | HTGVALVE-C | BO Mapper | (33) 021.CV-03S-- | 021 | cv | s | Afsluiter CV | Closing CV | Hot_Water_System | Warm water groep 1 | Hot water group 1 | Hot_Water_System | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
522 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.HTGVALVE-C | HTGVALVE-C | BO Mapper | (33) 022.CV-03S-- | 022 | cv | s | Afsluiter CV | Closing CV | Hot_Water_System | Warm water groep 2 | Hot water group 2 | Hot_Water_System | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
523 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SM3-C | SM3-C | BO Mapper | (33) 402.CV-03S-- | 402 | cv | s | Wisselklep bronnen open sturen | Switching valve sources open | Energy_Storage | Koudebron | Cold source | Energy_Storage | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
524 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM3-C | SM3-C | BO Mapper | (33) 404.CV-03S-- | 404 | cv | s | Wisselklep drogekoeler open sturen | Open the dry cooler diverter valve | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
525 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.HTG-C | HTG-C | BO Mapper | (33) 201.CV-03S-- | 201 | cv | s | Afsluiter CV | Closing CV | AHU | LBK 1 | AHU 1 | AHU | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
526 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.HTG-C | HTG-C | BO Mapper | (33) 202.CV-03S-- | 202 | cv | s | Afsluiter CV | Closing CV | AHU | LBK 2 | AHU 2 | AHU | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
527 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC011.ISOV-HTG-C | ISOV-HTG-C | BO Mapper | (33-0) 711.CV-03S-- | 711 | cv | s | Afsluiter open/dicht CV | Valve open/close CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
528 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC012.ISOV-HTG-C | ISOV-HTG-C | BO Mapper | (33-0) 712.CV-03S-- | 712 | cv | s | Afsluiter open/dicht CV | Valve open/close CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
529 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC013.ISOV-HTG-C | ISOV-HTG-C | BO Mapper | (33-0) 713.CV-03S-- | 713 | cv | s | Afsluiter open/dicht CV | Valve open/close CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
530 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.ISOV-HTG-C | ISOV-HTG-C | BO Mapper | (33-1) 719.CV-03S-- | 719 | cv | s | Afsluiter open/dicht CV | Valve open/close CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
531 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC020.ISOV-HTG-C | ISOV-HTG-C | BO Mapper | (33-1) 720.CV-03S-- | 720 | cv | s | Afsluiter open/dicht CV | Valve open/close CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
532 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC022.ISOV-HTG-C | ISOV-HTG-C | BO Mapper | (33-1) 722.CV-03S-- | 722 | cv | s | Afsluiter open/dicht CV | Valve open/close CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
533 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.ISOV-HTG-C | ISOV-HTG-C | BO Mapper | (33-1) 723.CV-03S-- | 723 | cv | s | Afsluiter open/dicht CV | Valve open/close CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
534 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC024.ISOV-HTG-C | ISOV-HTG-C | BO Mapper | (33-2) 724.CV-03S-- | 724 | cv | s | Afsluiter open/dicht CV | Valve open/close CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
535 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC025.ISOV-HTG-C | ISOV-HTG-C | BO Mapper | (33-2) 725.CV-03S-- | 725 | cv | s | Afsluiter open/dicht CV | Valve open/close CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
536 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC027.ISOV-HTG-C | ISOV-HTG-C | BO Mapper | (33-2) 727.CV-03S-- | 727 | cv | s | Afsluiter open/dicht CV | Valve open/close CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
537 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC028.ISOV-HTG-C | ISOV-HTG-C | BO Mapper | (33-2) 728.CV-03S-- | 728 | cv | s | Afsluiter open/dicht CV | Valve open/close CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
538 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC029.ISOV-HTG-C | ISOV-HTG-C | BO Mapper | (33-2) 729.CV-03S-- | 729 | cv | s | Afsluiter open/dicht CV | Valve open/close CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
539 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC031.ISOV-HTG-C | ISOV-HTG-C | BO Mapper | (33-2) 731.CV-03S-- | 731 | cv | s | Afsluiter open/dicht CV | Valve open/close CV | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
540 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC015.DPR3-AV-O | DPR3-AV-O | AO Mapper | (33-0) 715.VAV03V-- | 715 | vav | v | Afvoerlucht VAV-3sturing | Exhaust air VAV-3 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
541 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.DPR1-AV-O | DPR1-AV-O | AO Mapper | (33-1) 719.VAV03V-- | 719 | vav | v | Afvoerlucht VAV-1 sturing | Exhaust air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
542 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC022.DPR1-AV-O | DPR1-AV-O | AO Mapper | (33-1) 722.VAV03V-- | 722 | vav | v | Afvoerlucht VAV-1 sturing | Exhaust air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
543 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.DPR1-AV-O | DPR1-AV-O | AO Mapper | (33-1) 723.VAV03V-- | 723 | vav | v | Afvoerlucht VAV-1 sturing | Exhaust air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
544 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.EA FILT-A | EA FILT-A | MSV Mapper | (33) 201.PDA-04A-- | 201 | pda | a | Afvoerfilter vervuild | Drain filter dirty | AHU | LBK 1 | AHU 1 | AHU | Drukverschil alarm | Pressure difference alarm | Pressure_Alarm | Alarm | Alarm | Alarm
545 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Parameters.EA FILT-A | EA FILT-A | MSV Mapper | (33) 202.PDA-04A-- | 202 | pda | a | Afvoerfilter vervuild | Drain filter dirty | AHU | LBK 2 | AHU 2 | AHU | Drukverschil alarm | Pressure difference alarm | Pressure_Alarm | Alarm | Alarm | Alarm
546 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.CLG-CL-ALM | CLG-CL-ALM | MSV Mapper | (33) 201.CV-04A1- | 201 | cv | a | Afsluiter GKW niet dicht | Shut-off valve GKW not closed | AHU | LBK 1 | AHU 1 | AHU | Regelafsluiter | Regulating valve | Valve | Alarm | Alarm | Alarm
547 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Parameters.CLG-CL-ALM | CLG-CL-ALM | MSV Mapper | (33) 202.CV-04A1- | 202 | cv | a | Afsluiter GKW niet dicht | Shut-off valve GKW not closed | AHU | LBK 2 | AHU 2 | AHU | Regelafsluiter | Regulating valve | Valve | Alarm | Alarm | Alarm
548 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.Parameters.CLG-O-ALM | CLG-O-ALM | MSV Mapper | (33) 201.CV-04A2- | 201 | cv | a | Afsluiter GKW niet open | GKW shut-off valve not open | AHU | LBK 1 | AHU 1 | AHU | Regelafsluiter | Regulating valve | Valve | Alarm | Alarm | Alarm
549 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.Parameters.CLG-O-ALM | CLG-O-ALM | MSV Mapper | (33) 202.CV-04A2- | 202 | cv | a | Afsluiter GKW niet open | GKW shut-off valve not open | AHU | LBK 2 | AHU 2 | AHU | Regelafsluiter | Regulating valve | Valve | Alarm | Alarm | Alarm
550 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWL4-T | SCHWL4-T | AI Mapper | (33) 402.TT-04M-- | 402 | tt | m | Buffervat aanvoertemperatuur | Buffer tank supply temperature | Energy_Storage | Koudebron | Cold source | Energy_Storage | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
551 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CH1CHWR-T | CH1CHWR-T | AI Mapper | (33) 403.TT-04M-- | 403 | tt | m | Retouremperatuur WP-GKW | Return temperature WP-GKW | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
552 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CWS2-T | CWS2-T | AI Mapper | (33) 404.TT-04M-- | 404 | tt | m | Retourtemperatuur sec. | Return temperature sec. | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
553 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.EAHR-T | EAHR-T | AI Mapper | (33) 201.TT-04M-- | 201 | tt | m | Afblaasluchttemperatuur | Exhaust air temperature | AHU | LBK 1 | AHU 1 | AHU | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
554 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.EAHR-T | EAHR-T | AI Mapper | (33) 202.TT-04M-- | 202 | tt | m | Afblaasluchttemperatuur | Exhaust air temperature | AHU | LBK 2 | AHU 2 | AHU | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
555 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CLGVALVE-OP | CLGVALVE-OP | BI Mapper | (33) 021.CV-04O-- | 021 | cv | o | Vlinderklep GKW open | Butterfly valve GKW open | Hot_Water_System | Warm water groep 1 | Hot water group 1 | Hot_Water_System | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
556 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.CLGVALVE-OP | CLGVALVE-OP | BI Mapper | (33) 022.CV-04O-- | 022 | cv | o | Vlinderklep GKW open | Butterfly valve GKW open | Hot_Water_System | Warm water groep 2 | Hot water group 2 | Hot_Water_System | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
557 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SM4-OP | SM4-OP | BI Mapper | (33) 402.CV-04O-- | 402 | cv | o | Wisselklep bronnen open | Diverter valve sources open | Energy_Storage | Koudebron | Cold source | Energy_Storage | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
558 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM4-OP | SM4-OP | BI Mapper | (33) 404.CV-04O-- | 404 | cv | o | Wisselklep drogekoeler open | Drycooler diverter valve open | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
559 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.BK-04-O | BK-04-O | BI Mapper | (33) 203.BK-04O-- | 203 | bk | o | Brandkleppen open cluster 2-1 | Fire dampers open cluster 2-1 | AHU |  |  |  |  | Firedamper | Damper | Open | Open | Open_Close_Status
560 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CLGV-OP | CLGV-OP | BI Mapper | (33) 201.CV-04O-- | 201 | cv | o | Vlinderklep GKW open | Butterfly valve GKW open | AHU | LBK 1 | AHU 1 | AHU | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
561 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.CLGV-OP | CLGV-OP | BI Mapper | (33) 202.CV-04O-- | 202 | cv | o | Vlinderklep GKW open | Butterfly valve GKW open | AHU | LBK 2 | AHU 2 | AHU | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
562 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CLGVALVE-C | CLGVALVE-C | BO Mapper | (33) 021.CV-04S-- | 021 | cv | s | Afsluiter GKW | Valve GKW | Hot_Water_System | Warm water groep 1 | Hot water group 1 | Hot_Water_System | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
563 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.CLGVALVE-C | CLGVALVE-C | BO Mapper | (33) 022.CV-04S-- | 022 | cv | s | Afsluiter GKW | Valve GKW | Hot_Water_System | Warm water groep 2 | Hot water group 2 | Hot_Water_System | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
564 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SM4-C | SM4-C | BO Mapper | (33) 402.CV-04S-- | 402 | cv | s | Wisselklep bronnen open sturen | Switching valve sources open | Energy_Storage | Koudebron | Cold source | Energy_Storage | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
565 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM4-C | SM4-C | BO Mapper | (33) 404.CV-04S-- | 404 | cv | s | Wisselklep drogekoeler open sturen | Open the dry cooler diverter valve | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
566 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.CLG-C | CLG-C | BO Mapper | (33) 201.CV-04S-- | 201 | cv | s | Afsluiter GKW | Valve GKW | AHU | LBK 1 | AHU 1 | AHU | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
567 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.CLG-C | CLG-C | BO Mapper | (33) 202.CV-04S-- | 202 | cv | s | Afsluiter GKW | Valve GKW | AHU | LBK 2 | AHU 2 | AHU | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
568 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC011.ISOV-CLG-C | ISOV-CLG-C | BO Mapper | (33-0) 711.CV-04S-- | 711 | cv | s | Afsluiter open/dicht GKW | Valve open/close GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
569 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC012.ISOV-CLG-C | ISOV-CLG-C | BO Mapper | (33-0) 712.CV-04S-- | 712 | cv | s | Afsluiter open/dicht GKW | Valve open/close GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
570 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC013.ISOV-CLG-C | ISOV-CLG-C | BO Mapper | (33-0) 713.CV-04S-- | 713 | cv | s | Afsluiter open/dicht GKW | Valve open/close GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
571 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.ISOV-CLG-C | ISOV-CLG-C | BO Mapper | (33-1) 720.CV-04S-- | 720 | cv | s | Afsluiter open/dicht GKW | Valve open/close GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
572 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC020.ISOV-CLG-C | ISOV-CLG-C | BO Mapper | (33-1) 722.CV-04S-- | 722 | cv | s | Afsluiter open/dicht GKW | Valve open/close GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
573 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC022.ISOV-CLG-C | ISOV-CLG-C | BO Mapper | (33-1) 722.CV-04S-- | 722 | cv | s | Afsluiter open/dicht GKW | Valve open/close GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
574 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.ISOV-CLG-C | ISOV-CLG-C | BO Mapper | (33-1) 723.CV-04S-- | 723 | cv | s | Afsluiter open/dicht GKW | Valve open/close GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
575 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC024.ISOV-CLG-C | ISOV-CLG-C | BO Mapper | (33-2) 724.CV-04S-- | 724 | cv | s | Afsluiter open/dicht GKW | Valve open/close GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
576 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC025.ISOV-CLG-C | ISOV-CLG-C | BO Mapper | (33-2) 725.CV-04S-- | 725 | cv | s | Afsluiter open/dicht GKW | Valve open/close GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
577 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC027.ISOV-CLG-C | ISOV-CLG-C | BO Mapper | (33-2) 727.CV-04S-- | 727 | cv | s | Afsluiter open/dicht GKW | Valve open/close GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
578 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC028.ISOV-CLG-C | ISOV-CLG-C | BO Mapper | (33-2) 728.CV-04S-- | 728 | cv | s | Afsluiter open/dicht GKW | Valve open/close GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
579 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC029.ISOV-CLG-C | ISOV-CLG-C | BO Mapper | (33-2) 729.CV-04S-- | 729 | cv | s | Afsluiter open/dicht GKW | Valve open/close GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
580 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC031.ISOV-CLG-C | ISOV-CLG-C | BO Mapper | (33-2) 731.CV-04S-- | 731 | cv | s | Afsluiter open/dicht GKW | Valve open/close GKW | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
581 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWL5-T | SCHWL5-T | AI Mapper | (33) 402.TT-05M-- | 402 | tt | m | Buffervat retourtemperatuur | Buffer tank return temperature | Energy_Storage | Koudebron | Cold source | Energy_Storage | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
582 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.PCHWS-T | PCHWS-T | AI Mapper | (33) 403.TT-05M-- | 403 | tt | m | Retourtemperatuur algemeen GKW | Return temperature general GKW | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
583 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.PCHW-T | PCHW-T | AI Mapper | (33) 404.TT-05M-- | 404 | tt | m | Aanvoertemperatuur algemeen | General flow temperature | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
584 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.PHWE-T | PHWE-T | AI Mapper | (33) 201.TT-05M-- | 201 | tt | m | Aanvoeropnemer verwarmer/koeler | Heater/cooler flow sensor | AHU | LBK 1 | AHU 1 | AHU | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
585 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.PHWE-T | PHWE-T | AI Mapper | (33) 202.TT-05M-- | 202 | tt | m | Aanvoeropnemer verwarmer/koeler | Heater/cooler flow sensor | AHU | LBK 2 | AHU 2 | AHU | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
586 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM5-OP | SM5-OP | BI Mapper | (33) 404.CV-05O-- | 404 | cv | o | Wisselklep drogekoeler open | Drycooler diverter valve open | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
587 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.BK-05-O | BK-05-O | BI Mapper | (33) 203.BK-05O-- | 203 | bk | o | Brandkleppen open cluster 2-2 | Fire dampers open cluster 2-2 | AHU |  |  |  |  | Firedamper | Damper | Open | Open | Open_Close_Status
588 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM5-C | SM5-C | BO Mapper | (33) 404.CV-05S-- | 404 | cv | s | Wisselklep drogekoeler open sturen | Open the dry cooler diverter valve | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
589 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.ISO-FLR1-C | ISO-FLR1-C | BO Mapper | (33-1) 719.CV-05S-- | 719 | cv | s | Afsluiter vloerset 1&2 | Valve floor set 1&2 | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
590 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.ISO-FLR-C | ISO-FLR-C | BO Mapper | (33-1) 723.CV-05S-- | 723 | cv | s | Afsluiter vloerset 1 | Floor set valve 1 | Equipment |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
591 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Sturing bypass klep SL-O | Sturing bypass klep SL-O | AO Mapper | (33) 001.CV-05V-- | 001 | cv | v | Regelafsluiter overstort | Overflow control valve | Boiler | Ketel 1 | Boiler 1 | Boiler | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
592 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Sturing bypass klep SL-O | Sturing bypass klep SL-O | AO Mapper | (33) 122.CV-05V-- | 122 | cv | v | Regelafsluiter overstort | Overflow control valve | Chilled_Water_System | Gekoeld water groep 2 | Chilled water group 2 | Chilled_Water_System | Regelafsluiter | Regulating valve | Valve | Sturing | Control (analog signal) | Command
593 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.PCWR-T | PCWR-T | AI Mapper | (33) 403.TT-06M-- | 403 | tt | m | Retourtemperatuur algemeen CV | General CH return temperature | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
594 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWL6-T | SCHWL6-T | AI Mapper | (33) 402.TT-06M-- | 402 | tt | m | Buffervat temperatuur boven | Buffer tank temperature above | Energy_Storage | Koudebron | Cold source | Energy_Storage | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
595 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.PHWL-T | PHWL-T | AI Mapper | (33) 201.TT-06M-- | 201 | tt | m | Retourtemperatuur verwarmer/koeler | Heater/cooler return temperature | AHU | LBK 1 | AHU 1 | AHU | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
596 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.PHWL-T | PHWL-T | AI Mapper | (33) 202.TT-06M-- | 202 | tt | m | Retourtemperatuur verwarmer/koeler | Heater/cooler return temperature | AHU | LBK 2 | AHU 2 | AHU | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
597 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM6-OP | SM6-OP | BI Mapper | (33) 404.CV-06O-- | 404 | cv | o | Wisselklep drogekoeler open | Drycooler diverter valve open | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
598 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.BK-06-O | BK-06-O | BI Mapper | (33) 203.BK-06O-- | 203 | bk | o | Brandkleppen open cluster 3-1 | Fire dampers open cluster 3-1 | AHU |  |  |  |  | Firedamper | Damper | Open | Open | Open_Close_Status
599 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM6-C | SM6-C | BO Mapper | (33) 404.CV-06S-- | 404 | cv | s | Wisselklep drogekoeler open sturen | Open the dry cooler diverter valve | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
600 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWL7-T | SCHWL7-T | AI Mapper | (33) 402.TT-07M-- | 402 | tt | m | Buffervat temperatuur midden boven | Buffer tank temperature top center | Energy_Storage | Koudebron | Cold source | Energy_Storage | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
601 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CW7-T | CW7-T | AI Mapper | (33) 403.TT-07M-- | 403 | tt | m | Buffervat aanvoertemperatuur/boven | Buffer tank flow temperature/above | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
602 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.HR-T | HR-T | AI Mapper | (33) 201.TT-07M-- | 201 | tt | m | Aanzuigtemp na warmtewiel | Suction temp after heat exchanger | AHU | LBK 1 | AHU 1 | AHU | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
603 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC006.HR-T | HR-T | AI Mapper | (33) 202.TT-07M-- | 202 | tt | m | Aanzuigtemp na warmtewiel | Suction temp after heat exchanger | AHU | LBK 2 | AHU 2 | AHU | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
604 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM7-OP | SM7-OP | BI Mapper | (33) 404.CV-07O-- | 404 | cv | o | Wisselklep drogekoeler open | Drycooler diverter valve open | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Open | Open | Open_Close_Status
605 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.BK-07-O | BK-07-O | BI Mapper | (33) 203.BK-07O-- | 203 | bk | o | Brandkleppen open cluster 3-2 | Fire dampers open cluster 3-2 | AHU |  |  |  |  | Firedamper | Damper | Open | Open | Open_Close_Status
606 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC005.SM7-C | SM7-C | BO Mapper | (33) 404.CV-07S-- | 404 | cv | s | Wisselklep drogekoeler open sturen | Open the dry cooler diverter valve | Energy_Storage |  |  |  | Regelafsluiter | Regulating valve | Valve | Schakelen | Switch | Status
607 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.FD-C | FD-C | BO Mapper | (33) 203.BK-07S-- | 203 | bk | s | Brandkleppen opensturen | Open fire dampers | AHU |  |  |  |  | Firedamper | Damper | Schakelen | Switch | Status
608 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CW8-T | CW8-T | AI Mapper | (33) 403.TT-08M-- | 403 | tt | m | Buffervat retourtemperatuur/midden | Buffer tank return temperature/middle | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
609 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWL8-T | SCHWL8-T | AI Mapper | (33) 402.TT-08M-- | 402 | tt | m | Buffervat temperatuur midden onder | Buffer tank temperature bottom center | Energy_Storage | Koudebron | Cold source | Energy_Storage | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
610 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.SCHWL9-T | SCHWL9-T | AI Mapper | (33) 402.TT-09M-- | 402 | tt | m | Buffervat temperatuur onder | Buffer tank temperature below | Energy_Storage | Koudebron | Cold source | Energy_Storage | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
611 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.CW9-T | CW9-T | AI Mapper | (33) 403.TT-09M-- | 403 | tt | m | Buffervat retourtemperatuur/onder | Buffer tank return temperature/bottom | Energy_Storage |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
612 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp minimum flow ontladen | Setp minimum flow ontladen | AV Mapper | (33) 803.NI--1001 | 803 | ni |  | Setp. minimum flow ontladen | Setp. discharge minimum flow | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
613 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.PSK Bronnen 0=Uit 1=A 2=H 3=Vull | PSK Bronnen 0=Uit 1=A 2=H 3=Vull | MSV Mapper | (33) 803.NI--1002 | 803 | ni |  | PSK 0=Uit,1=Aut,2=Hand,3=Vul | PSK 0=Off,1=Aut,2=Manual,3=Fill | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
614 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.PSK Spuien 0=Uit 1=KB 2=WB | PSK Spuien 0=Uit 1=KB 2=WB | MSV Mapper | (33) 803.NI--1003 | 803 | ni |  | PSK Spuien 0=Uit, 1=KB, 2=WB | PSK Bleed 0=Off, 1=KB, 2=WB | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
615 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp uitsch druk laden-ontladen | Setp uitsch druk laden-ontladen | AV Mapper | (33) 803.NI--1004 | 803 | ni |  | Setp. uitschakeldruk laden-ontladen | Setp. charge-discharge switch-off pressure | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
616 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Max tijdsduur vullen | Max tijdsduur vullen | AV Mapper | (33) 803.NI--1005 | 803 | ni |  | Max. tijdsduur vullen | max. fill time | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
617 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Ontladen vraag uit gebouw (PtP) | Ontladen vraag uit gebouw (PtP) | MSV Mapper | (33) 803.NI--1006 | 803 | ni |  | Ontladen vraag uit gebouw (PtP) | Unloaded demand from building (PtP) | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
618 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp insch druk drukhandhaving | Setp insch druk drukhandhaving | AV Mapper | (33) 803.NI--1007 | 803 | ni |  | Setp. inschakeldruk drukhandhaving | Setp. cut-in pressure pressure maintenance | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
619 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp min druk laden-ontladen | Setp min druk laden-ontladen | AV Mapper | (33) 803.NI--1008 | 803 | ni |  | Setp. min. druk laden-ontladen | Setp. min. charge-discharge pressure | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
620 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Invertr min druk laden-ontladen | Invertr min druk laden-ontladen | AV Mapper | (33) 803.NI--1009 | 803 | ni |  | Invertr. min. druk laden-ontladen | inverter min. charge-discharge pressure | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
621 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp maximum druk | Setp maximum druk | AV Mapper | (33) 803.NI--1010 | 803 | ni |  | Setp. maximum druk | Setp. maximum pressure | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
622 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Rust nivo KB (LCT) | Rust nivo KB (LCT) | AV Mapper | (33) 803.NI--1011 | 803 | ni |  | Rust nivo KB (LCT) | Rest level KB (LCT) | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
623 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp uitsch druk stop spuien | Setp uitsch druk stop spuien | AV Mapper | (33) 803.NI--1012 | 803 | ni |  | Setp. uitschakeldruk proc. stop spuien | Setp. cut-out pressure proc. stop spitting | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
624 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.PSK Hand 0=R 1=Lad 2=Ontlad 3=Sp | PSK Hand 0=R 1=Lad 2=Ontlad 3=Sp | MSV Mapper | (33) 803.NI--1013 | 803 | ni |  | PSK H 0=Rust, 1=Lad, 2=Ontl, 3=Spui | PSK H 0=Rest, 1=Load, 2=Discharge, 3=Flow | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
625 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Rust nivo WB (LCT) | Rust nivo WB (LCT) | AV Mapper | (33) 803.NI--1014 | 803 | ni |  | Rust nivo WB (LCT) | Rest level WB (LCT) | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
626 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Laden vraag uit gebouw (PtP) | Laden vraag uit gebouw (PtP) | MSV Mapper | (33) 803.NI--1015 | 803 | ni |  | Laden vraag uit gebouw (PtP) | Load demand from building (PtP) | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
627 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp freqeuntie KB bij spuien | Setp freqeuntie KB bij spuien | AV Mapper | (33) 803.NI--1016 | 803 | ni |  | Setp. freqeuntie KB bij spuien | Setp. frequency KB at discharge | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
628 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Vertraging melding flowbewaking | Vertraging melding flowbewaking | AV Mapper | (33) 803.NI--1017 | 803 | ni |  | Vertraging melding flowbewaking | Delay flow monitoring notification | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
629 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.PSK Gew flow 0=Uit 1=Aut 2=Hand | PSK Gew flow 0=Uit 1=Aut 2=Hand | MSV Mapper | (33) 803.NI--1018 | 803 | ni |  | PSK Gew. flow 0=Uit, 1=Aut, 2=Hand | PSK Wt. flow 0=Off, 1=Aut, 2=Manual | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
630 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Minimale tijd rust | Minimale tijd rust | AV Mapper | (33) 803.NI--1019 | 803 | ni |  | Minimale tijd rust | Minimum rest time | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
631 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp max regelafw laden-ontladen | Setp max regelafw laden-ontladen | AV Mapper | (33) 803.NI--1020 | 803 | ni |  | Setp. max. regelafw. laden-ontladen | Setp. max. line dev. charge-discharge | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
632 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Max keer drukhandhaving in 24h | Max keer drukhandhaving in 24h | AV Mapper | (33) 803.NI--1021 | 803 | ni |  | Max. keer drukhandhaving in 24h | max. times pressure maintenance in 24h | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
633 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Gewenste flow hand bedrijf | Gewenste flow hand bedrijf | AV Mapper | (33) 803.NI--1022 | 803 | ni |  | Gewenste flow hand bedrijf | Desired flow hand holding | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
634 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp uitsch druk drukhandhaving | Setp uitsch druk drukhandhaving | AV Mapper | (33) 803.NI--1023 | 803 | ni |  | Setp. uitschakeldruk drukhandhaving | Setp. cut-out pressure pressure maintenance | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
635 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Max tijdsduur drukhandhaving | Max tijdsduur drukhandhaving | AV Mapper | (33) 803.NI--1024 | 803 | ni |  | Max. tijdsduur drukhandhaving | max. duration of pressure maintenance | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
636 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp freqeuntie WB bij spuien | Setp freqeuntie WB bij spuien | AV Mapper | (33) 803.NI--1025 | 803 | ni |  | Setp. freqeuntie WB bij spuien | Setp. frequency WB at discharge | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
637 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.FLow gebouwzijdig | FLow gebouwzijdig | AV Mapper | (33) 803.NI--1026 | 803 | ni |  | Flow gebouwzijdig | Flow building side | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
638 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp minimum flow laden | Setp minimum flow laden | AV Mapper | (33) 803.NI--1027 | 803 | ni |  | Minimum flow laden | Load minimum flow | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
639 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Insch vertr injectieklep KB | Insch vertr injectieklep KB | AV Mapper | (33) 803.NI--1028 | 803 | ni |  | Insch. vertr. injectieklep KB | switch on delay injection valve KB | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
640 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Insch vertr injectieklep WB | Insch vertr injectieklep WB | AV Mapper | (33) 803.NI--1029 | 803 | ni |  | Insch. vertr. injectieklep WB | switch on delay injection valve WB | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
641 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp max nivo KB bij laden | Setp max nivo KB bij laden | AV Mapper | (33) 803.NI--1030 | 803 | ni |  | Setp. max. nivo KB bij laden | Setp. max. level KB when loading | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
642 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp max nivo WB bij ontladen | Setp max nivo WB bij ontladen | AV Mapper | (33) 803.NI--1031 | 803 | ni |  | Setp. max. nivo WB bij ontladen | Setp. max. level WB when discharged | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
643 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp min nivo KB bij ontladen | Setp min nivo KB bij ontladen | AV Mapper | (33) 803.NI--1032 | 803 | ni |  | Setp. min. nivo KB bij ontladen | Setp. min. level KB at discharge | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
644 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp min nivo KB bij spuien | Setp min nivo KB bij spuien | AV Mapper | (33) 803.NI--1033 | 803 | ni |  | Setp. min. nivo KB bij spuien | Setp. min. level KB when flushing | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
645 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp min nivo WB bij laden | Setp min nivo WB bij laden | AV Mapper | (33) 803.NI--1034 | 803 | ni |  | Setp. min. nivo WB bij laden | Setp. min. level WB when charging | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
646 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp min nivo WB bij spuien | Setp min nivo WB bij spuien | AV Mapper | (33) 803.NI--1035 | 803 | ni |  | Setp. min. nivo WB bij spuien | Setp. min. level WB when flushing | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
647 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp onderhoud nivo KB laden | Setp onderhoud nivo KB laden | AV Mapper | (33) 803.NI--1036 | 803 | ni |  | Setp. onderhoud nivo KB bij laden | Setp. maintenance level KB when loading | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
648 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp onderhoud nivo KB ontladen | Setp onderhoud nivo KB ontladen | AV Mapper | (33) 803.NI--1037 | 803 | ni |  | Setp. onderhoud nivo KB bij ontladen | Setp. maintenance level KB on discharge | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
649 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp onderhoud nivo WB laden | Setp onderhoud nivo WB laden | AV Mapper | (33) 803.NI--1038 | 803 | ni |  | Setp. onderhoud nivo WB bij laden | Setp. maintenance level WB when loading | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
650 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Setp onderhoud nivo WB ontladen | Setp onderhoud nivo WB ontladen | AV Mapper | (33) 803.NI--1039 | 803 | ni |  | Setp. onderhoud nivo WB bij ontladen | Setp. maintenance level WB when discharging | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
651 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Spui programma | Spui programma | MSV Mapper | (33) 803.NI--1040 | 803 | ni |  | Spui programma 0=uit, 1=KB, 2=WB | Bleed program 0=off, 1=KB, 2=WB | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
652 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Tijdsduur spuien | Tijdsduur spuien | AV Mapper | (33) 803.NI--1041 | 803 | ni |  | Tijdsduur spuien | Spraying time | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
653 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Uitsch vertr injectieklep KB | Uitsch vertr injectieklep KB | AV Mapper | (33) 803.NI--1042 | 803 | ni |  | Uitsch. vertr. injectieklep KB | Disable delay injection valve KB | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
654 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Uitsch vertr injectieklep WB | Uitsch vertr injectieklep WB | AV Mapper | (33) 803.NI--1043 | 803 | ni |  | Uitsch. vertr. injectieklep WB | Disable delay injection valve WB | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
655 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Vertr melding flowbew spuien WB | Vertr melding flowbew spuien WB | AV Mapper | (33) 803.NI--1044 | 803 | ni |  | Vertr. melding flowbew. spuien WB | Delay flow monitor message flush WB | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
656 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Datum onderhoudsmelding KB | Datum onderhoudsmelding KB | MSV Mapper | (33) 803.NI--1045 | 803 | ni |  | Datum onderhoudsmelding KB | Date maintenance notification KB | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
657 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.Datum onderhoudsmelding WB | Datum onderhoudsmelding WB | MSV Mapper | (33) 803.NI--1046 | 803 | ni |  | Datum onderhoudsmelding WB | Date maintenance notification WB | Breaker_Panel |  |  |  |  | Netwerk input. Peer to Peer.
658 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.ZN1-H | ZN1-H | AI Mapper | (33) 905.MT-10M-- | 905 | mt | m | Ruimtetvocht SER 1 | Space moisture SER 1 | Server_Room | SER/MER meldingen | MER = Main Equipment Room, SER = Satellite Equipment Room | Server_Room | Vocht transmitter | Moisture transmitter | Humidity_Sensor | Meting | Measurement | Sensor
659 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.ZN1-T | ZN1-T | AI Mapper | (33) 905.TT-10M-- | 905 | tt | m | Ruimtetemperatuur SER 1 | Room temperature SER 1 | Server_Room | SER/MER meldingen | MER = Main Equipment Room, SER = Satellite Equipment Room | Server_Room | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
660 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC011.ZN1-T | ZN1-T | AI Mapper | (33-0) 711.TT-10M-- | 711 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
661 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC011.ZN1-Q | ZN1-Q | AI Mapper | (33-0) 711.QT-10M-- | 711 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
662 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC012.ZN1-T | ZN1-T | AI Mapper | (33-0) 712.TT-10M-- | 712 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
663 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC012.ZN1-Q | ZN1-Q | AI Mapper | (33-0) 712.QT-10M-- | 712 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
664 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC013.ZN1-T | ZN1-T | AI Mapper | (33-0) 713.TT-10M-- | 713 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
665 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC013.ZN1-Q | ZN1-Q | AI Mapper | (33-0) 713.QT-10M-- | 713 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
666 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC016.ZN1-T | ZN1-T | AI Mapper | (33-0) 716.TT-10M-- | 716 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
667 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC016.ZN1-Q | ZN1-Q | AI Mapper | (33-0) 716.QT-10M-- | 716 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
668 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC017.ZN1-T | ZN1-T | AI Mapper | (33-0) 717.TT-10M-- | 717 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
669 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC017.ZN1-Q | ZN1-Q | AI Mapper | (33-0) 717.QT-10M-- | 717 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
670 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC018.ZN1-T | ZN1-T | AI Mapper | (33-0) 718.TT-10M-- | 718 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
671 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC018.ZN1-Q | ZN1-Q | AI Mapper | (33-0) 718.QT-10M-- | 718 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
672 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.ZN1-T | ZN1-T | AI Mapper | (33-1) 719.TT-10M-- | 719 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
673 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.ZN1-Q | ZN1-Q | AI Mapper | (33-1) 719.QT-10M-- | 719 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
674 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC020.ZN1-T | ZN1-T | AI Mapper | (33-1) 720.TT-10M-- | 720 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
675 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC020.ZN1-Q | ZN1-Q | AI Mapper | (33-1) 720.QT-10M-- | 720 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
676 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC021.ZN1-T | ZN1-T | AI Mapper | (33-1) 721.TT-10M-- | 721 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
677 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC021.ZN1-Q | ZN1-Q | AI Mapper | (33-1) 721.QT-10M-- | 721 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
678 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC022.ZN1-T | ZN1-T | AI Mapper | (33-1) 722.TT-10M-- | 722 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
679 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC022.ZN1-Q | ZN1-Q | AI Mapper | (33-1) 722.QT-10M-- | 722 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
680 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.ZN1-T | ZN1-T | AI Mapper | (33-1) 723.TT-10M-- | 723 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
681 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.ZN1-Q | ZN1-Q | AI Mapper | (33-1) 723.QT-10M-- | 723 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
682 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC024.ZN1-T | ZN1-T | AI Mapper | (33-2) 724.TT-10M-- | 724 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
683 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC024.ZN1-Q | ZN1-Q | AI Mapper | (33-2) 724.QT-10M-- | 724 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
684 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC025.ZN1-T | ZN1-T | AI Mapper | (33-2) 725.TT-10M-- | 725 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
685 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC025.ZN1-Q | ZN1-Q | AI Mapper | (33-2) 725.QT-10M-- | 725 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
686 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC026.ZN1-T | ZN1-T | AI Mapper | (33-2) 726.TT-10M-- | 726 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
687 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC026.ZN1-Q | ZN1-Q | AI Mapper | (33-2) 726.QT-10M-- | 726 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
688 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC027.ZN1-T | ZN1-T | AI Mapper | (33-2) 727.TT-10M-- | 727 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
689 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC028.ZN1-T | ZN1-T | AI Mapper | (33-2) 728.TT-10M-- | 728 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
690 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC028.ZN1-Q | ZN1-Q | AI Mapper | (33-2) 728.QT-10M-- | 728 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
691 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC029.ZN1-T | ZN1-T | AI Mapper | (33-2) 729.TT-10M-- | 729 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
692 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC029.ZN1-Q | ZN1-Q | AI Mapper | (33-2) 729.QT-10M-- | 729 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
693 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC030.ZN1-T | ZN1-T | AI Mapper | (33-2) 730.TT-10M-- | 730 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
694 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC030.ZN1-Q | ZN1-Q | AI Mapper | (33-2) 730.QT-10M-- | 730 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
695 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC031.ZN1-T | ZN1-T | AI Mapper | (33-2) 731.TT-10M-- | 731 | tt | m | Ruimtetemperauur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
696 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC031.ZN1-Q | ZN1-Q | AI Mapper | (33-2) 731.QT-10M-- | 731 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
697 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC027.ZN1-Q | ZN1-Q | AI Mapper | (33-2) 727.QT-10M-- | 727 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
698 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC011.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-0) 711.TT-10M1- | 711 | tt | m | Gemiddelde ruimtetemperatuur (33-0) 711.TT-10M1- | Average room temperature (33-0) 711.TT-10M1- | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
699 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC012.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-0) 712.TT-10M1- | 712 | tt | m | Gemiddelde ruimtetemperatuur | Average room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
700 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC013.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-0) 713.TT-10M1- | 713 | tt | m | Gemiddelde ruimtetemperatuur | Average room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
701 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC016.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-0) 716.TT-10M1- | 716 | tt | m | Gemiddelde ruimtetemperatuur | Average room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
702 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC017.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-0) 717.TT-10M1- | 717 | tt | m | Gemiddelde ruimtetemperatuur | Average room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
703 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC018.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-0) 718.TT-10M1- | 718 | tt | m | Gemiddelde ruimtetemperatuur | Average room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
704 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC021.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-1) 721.TT-10M1- | 721 | tt | m | Gemiddelde ruimtetemperatuur | Average room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
705 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC025.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-2) 725.TT-10M1- | 725 | tt | m | Gemiddelde ruimtetemperatuur | Average room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
706 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC026.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-2) 726.TT-10M1- | 726 | tt | m | Gemiddelde ruimtetemperatuur | Average room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
707 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC029.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-2) 729.TT-10M1- | 729 | tt | m | Gemiddelde ruimtetemperatuur | Average room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
708 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC030.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-2) 730.TT-10M1- | 730 | tt | m | Gemiddelde ruimtetemperatuur | Average room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
709 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-1) 719.TT-10M1- | 719 | tt | m | Gemiddelde ruimtetemperatuur | Average room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
710 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC022.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-1) 722.TT-10M1- | 722 | tt | m | Gemiddelde ruimtetemperatuur | Average room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
711 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC024.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-2) 724.TT-10M1- | 724 | tt | m | Gemiddelde ruimtetemperatuur | Average room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
712 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC027.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-2) 727.TT-10M1- | 727 | tt | m | Gemiddelde ruimtetemperatuur | Average room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
713 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC028.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-2) 728.TT-10M1- | 728 | tt | m | Gemiddelde ruimtetemperatuur | Average room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
714 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC031.Parameters.ZN-T-GEM | ZN-T-GEM | AV Mapper | (33-2) 731.TT-10M1- | 731 | tt | m | Gemiddelde ruimtetemperatuur | Average room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
715 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC011.Network Inputs.I-ZN-SP-OCC | I-ZN-SP-OCC | AV Mapper | (33-0) 711.TC-10W-- | 711 | tc | w | Rmt setpoint (occ) | Rmt setpoint (occ) | Equipment |  |  |  | Temperatuurregeling | Temperature regulation | Temperature | Werksetpunt | Operation set point | Setpoint
716 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC011.Network Outputs.O-CO2-X1 | O-CO2-X1 | AV Mapper | (33-0) 711.QC-10W-- | 711 | qc | w | Werksetpoint | Working set point | Equipment |  |  |  |  | Air quality | Air_Quality_Sensor | Werksetpunt | Operation set point | Setpoint
717 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.ZN2-H | ZN2-H | AI Mapper | (33) 905.MT-11M-- | 905 | mt | m | Ruimtetvocht SER 2 | Space moisture SER 2 | Server_Room | SER/MER meldingen | MER = Main Equipment Room, SER = Satellite Equipment Room | Server_Room | Vocht transmitter | Moisture transmitter | Humidity_Sensor | Meting | Measurement | Sensor
718 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.ZN2-T | ZN2-T | AI Mapper | (33) 905.TT-11M-- | 905 | tt | m | Ruimtetemperatuur DC ruimte (SER1) | Room temperature DC room (SER1) | Server_Room | SER/MER meldingen | MER = Main Equipment Room, SER = Satellite Equipment Room | Server_Room | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
719 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC011.ZN2-Q | ZN2-Q | AI Mapper | (33-0) 711.QT-11M-- | 711 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
720 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC011.ZN2-T | ZN2-T | AI Mapper | (33-0) 711.TT-11M-- | 711 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
721 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC012.ZN2-Q | ZN2-Q | AI Mapper | (33-0) 712.QT-11M-- | 712 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
722 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC012.ZN2-T | ZN2-T | AI Mapper | (33-0) 712.TT-11M-- | 712 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
723 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC013.ZN2-Q | ZN2-Q | AI Mapper | (33-0) 713.QT-11M-- | 713 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
724 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC013.ZN2-T | ZN2-T | AI Mapper | (33-0) 713.TT-11M-- | 713 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
725 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC016.ZN2-Q | ZN2-Q | AI Mapper | (33-0) 716.QT-11M-- | 716 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
726 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC016.ZN2-T | ZN2-T | AI Mapper | (33-0) 716.TT-11M-- | 716 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
727 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC017.ZN2-Q | ZN2-Q | AI Mapper | (33-0) 717.QT-11M-- | 717 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
728 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC017.ZN2-T | ZN2-T | AI Mapper | (33-0) 717.TT-11M-- | 717 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
729 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC018.ZN2-Q | ZN2-Q | AI Mapper | (33-0) 718.QT-11M-- | 718 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
730 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC018.ZN2-T | ZN2-T | AI Mapper | (33-0) 718.TT-11M-- | 718 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
731 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.ZN2-Q | ZN2-Q | AI Mapper | (33-1) 719.QT-11M-- | 719 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
732 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC019.ZN2-T | ZN2-T | AI Mapper | (33-1) 719.TT-11M-- | 719 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
733 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC020.ZN2-Q | ZN2-Q | AI Mapper | (33-1) 720.QT-11M-- | 720 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
734 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC020.ZN2-T | ZN2-T | AI Mapper | (33-1) 720.TT-11M-- | 720 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
735 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC021.ZN2-Q | ZN2-Q | AI Mapper | (33-1) 721.QT-11M-- | 721 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
736 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC021.ZN2-T | ZN2-T | AI Mapper | (33-1) 721.TT-11M-- | 721 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
737 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC022.ZN2-Q | ZN2-Q | AI Mapper | (33-1) 722.QT-11M-- | 722 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
738 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC022.ZN2-T | ZN2-T | AI Mapper | (33-1) 722.TT-11M-- | 722 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
739 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.ZN2-Q | ZN2-Q | AI Mapper | (33-1) 723.QT-11M-- | 723 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
740 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC023.ZN2-T | ZN2-T | AI Mapper | (33-1) 723.TT-11M-- | 723 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
741 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC024.ZN2-Q | ZN2-Q | AI Mapper | (33-2) 724.QT-11M-- | 724 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
742 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC024.ZN2-T | ZN2-T | AI Mapper | (33-2) 724.TT-11M-- | 724 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
743 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC025.ZN2-Q | ZN2-Q | AI Mapper | (33-2) 725.QT-11M-- | 725 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
744 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC025.ZN2-T | ZN2-T | AI Mapper | (33-2) 725.TT-11M-- | 725 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
745 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC026.ZN2-Q | ZN2-Q | AI Mapper | (33-2) 726.QT-11M-- | 726 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
746 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC026.ZN2-T | ZN2-T | AI Mapper | (33-2) 726.TT-11M-- | 726 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
747 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC027.ZN2-Q | ZN2-Q | AI Mapper | (33-2) 727.QT-11M-- | 727 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
748 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC027.ZN2-T | ZN2-T | AI Mapper | (33-2) 727.TT-11M-- | 727 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
749 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC028.ZN2-Q | ZN2-Q | AI Mapper | (33-2) 728.QT-11M-- | 728 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
750 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC028.ZN2-T | ZN2-T | AI Mapper | (33-2) 728.TT-11M-- | 728 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
751 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC029.ZN2-Q | ZN2-Q | AI Mapper | (33-2) 729.QT-11M-- | 729 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
752 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC029.ZN2-T | ZN2-T | AI Mapper | (33-2) 729.TT-11M-- | 729 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
753 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC030.ZN2-Q | ZN2-Q | AI Mapper | (33-2) 730.QT-11M-- | 730 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
754 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC030.ZN2-T | ZN2-T | AI Mapper | (33-2) 730.TT-11M-- | 730 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
755 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC031.ZN2-Q | ZN2-Q | AI Mapper | (33-2) 731.QT-11M-- | 731 | qt | m | Ruimtekwaliteit | Space quality | Equipment |  |  |  | Lucht kwaliteit | Air quality | Air_Quality_Sensor | Meting | Measurement | Sensor
756 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC031.ZN2-T | ZN2-T | AI Mapper | (33-2) 731.TT-11M-- | 731 | tt | m | Ruimtetemperatuur | Room temperature | Equipment |  |  |  | Temperatuur transmitter | Temperature transmitter | Temperature_Sensor | Meting | Measurement | Sensor
757 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC012.OCC-S | OCC-S | BI Mapper | (33-0) 712.PIR01B-- | 712 | pir | b | Aanwezigheid | Presence | Equipment |  |  |  | Passief infrarood | Passive infrared PIR | PIR_Sensor | Bedrijfsmelding | Operation status | Status
758 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC012.DPR1-TV-O | DPR1-TV-O | AO Mapper | (33-0) 712.VAV01V-- | 712 | vav | v | Toevoerlucht VAV-1 sturing | Supply air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
759 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC015.DPR1-AV-O | DPR1-AV-O | AO Mapper | (33-0) 715.VAV01V-- | 715 | vav | v | Afvoerlucht VAV-1 sturing | Exhaust air VAV-1 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
760 | XXXXXXXXXXXXXXXXXXXX/FCB.FEC012.DPR2-TV-O | DPR2-TV-O | AO Mapper | (33-0) 712.VAV02V-- | 712 | vav | v | Toevoerlucht VAV-2 sturing | Supply air VAV-2 control | Equipment |  |  |  |  | Variable Air Volume box | VAV | Sturing | Control (analog signal) | Command
761 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Freq reg bronpompen storing | Freq reg bronpompen storing | BI Mapper | (33) 413.BP---A1- | 413 | bp | a | Freq.reg.bronpompen storing | Freq.control brine pumps failure | Energy_Storage |  |  |  | Bronpomp | Well pump | Water_Pump | Alarm | Alarm | Alarm
762 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Freq reg bronpompen bedrijf | Freq reg bronpompen bedrijf | BI Mapper | (33) 413.BP---B-- | 413 | bp | b | Freq.reg.bronpompen bedrijf | Freq.reg.well pumps operation | Energy_Storage |  |  |  | Bronpomp | Well pump | Water_Pump | Bedrijfsmelding | Operation status | Status
763 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Network Inputs.I-Flow CV | I-Flow CV | AV Mapper | (33) 001.FQT01-M1 | 001 | fqt | m | Flow CV (PtP) | Flow CV (PtP) | Boiler | Ketel 1 | Boiler 1 | Boiler |  | Energymeter | Electrical_Meter | Meting | Measurement | Sensor
764 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Freq reg bronpompen vrijgave | Freq reg bronpompen vrijgave | BO Mapper | (33) 413.BP---S-- | 413 | bp | s | Freq.reg.bronpompen vrijgave | Freq.reg. brine pumps release | Energy_Storage |  |  |  | Bronpomp | Well pump | Water_Pump | Schakelen | Switch | Status
765 | XXXXXXXXXXXXXXXXXXXX/FCB.Local Application.Freq reg bronpompen sturing | Freq reg bronpompen sturing | AO Mapper | (33) 410.BP---V-- | 410 | bp | v | Freq.reg.bronpompen sturing | Freq.reg. source pumps control | Energy_Storage |  |  |  | Bronpomp | Well pump | Water_Pump | Sturing | Control (analog signal) | Command